- Coal Handler

- Control Narrative

Table of Contents

Coal Handler Overview	4

Major Equipment	5

Discrete Instrument and Control Point Listing	5

Operator Controls	8

Local Operation	11

Manual Mode Operation	12

Automatic Mode Operation	13

Device Operation	15

Unloading Feeder	15

Reclaim Feeder	16

Bucket Elevator	16

Diverter Gate 1	18

Conveyor 1	19

Diverter Gate 2	20

Conveyor 2	21

Diverter Gate 3	22

Conveyor 3	23

# Coal Handler Overview

The coal handling system transfers coal from either a truck hopper or the coal pile to one of three bunkers. Purchased coal is unloaded into a truck dump hopper. The truck trailer tilts up, allowing the coal to fall out into a hopper, where it is conveyed to the reclaim coal pile or to one of the coal bunkers inside the power plant. When the truck dump hopper is empty, the coal must come from the reclaim hopper, which is loaded from the reclaim coal pile. The primary control objective of the coal handling unit is to convey coal from one of two sources (truck hopper or reclaim hopper) to one of four destinations (reclaim, bunker 1, bunker 2, or bunker 3). Normal operation is intermittent, running only when a truck needs to unload or a coal bunker is nearly empty.

The system has three operation modes: (1) local jog, (2) manual, and (3) automatic.

Local Jog: A local station at each major piece of equipment (feeders, bucket elevator, gates, and conveyors) provides local jog operation for maintenance and test. Equipment interlock is not provided, though the E-Stop and local safety switches will override the jog operation. The operator must hold the switch in the jog position to run the equipment. The switch at the local station must be in the "Rem" position for the manual and automatic operation modes.

Manual: The operator individually sets the diverter gate positions and then individually starts the conveyors, bucket elevator, and feeder. The operator must start with the piece of equipment closest to the destination (lowering well or bunker) and proceed to the source (one of the feeders). Interlocks prevent the operator from starting in the wrong order.

Automatic: The operator individually sets the diverter gate positions to establish the source-to-destination path. When the operator initiates a start (System Auto Control switch), the conveyors, bucket elevator, and appropriate feeders are started in the appropriate order. When the operator initiates a purge/stop (System Auto Control switch), the conveyors, bucket elevator, and appropriate feeders are stopped in the appropriate order with an intervening delay to allow material to be cleared from the equipment. Also, when the destination bunker is low (currently only bunker 3 has a low sensor) and the path to bunker 3 is selected, an automatic start is initiated. When the destination bunker is full (currently only bunker 3), an automatic purge is initiated.

Alarms are reported on the OI Panel, described in the document "Coal Handler OI Panel Description."

# Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| BEM | Bucket Elevator Motor | Conveys coal from the vibrating feeders to a point over diverter gate #1. |
| BUNK1 | Coal Bunker #1 | Stores coal for use in boiler #1. |
| BUNK2 | Coal Bunker #2 | Stores coal for use in boiler #2. |
| BUNK3 | Coal Bunker #3 | Stores coal for use in boiler #3. |
| C1 | Conveyor #1 | Conveys coal from diverter gate #1 to a point over diverter gate #2. |
| C2 | Conveyor #2 | Conveys coal from diverter gate #2 to a point over diverter gate #3. |
| C3 | Conveyor #3 | Conveys coal from diverter gate #3 to bunker #3. |
| G1 | Diverter Gate #1 | Directs coal from the top of the bucket elevator to either conveyor #1 or to the reclaim coal pile. |
| G2 | Diverter Gate #2 | Directs coal from the end of conveyor #1 to either bunker #1 or to conveyor #2. |
| G3 | Diverter Gate #3 | Directs coal from the end of conveyor #2 to either bunker #2 or to conveyor #3. |
| RFM | Reclaim Vibratory Feeder Motor | Vibrating feeder that transfers coal from the reclaim coal pile unloading hopper to the bucket elevator. |
| UFM | Unloading Vibratory Feeder Motor | Vibrating feeder that transfers coal from the truck unloading hopper to the bucket elevator. |

# Discrete Instrument and Control Point Listing

| TAG | TYPE | DESCRIPTION | PURPOSE | INTERLOCKS |
| --- | --- | --- | --- | --- |
| B1FLP | Level Switch | Bunker 1 Full Level Switch | Indicates bunker #1 is full and can be shut down normally. |  |
| B1HLP | Level Switch | Bunker 1 High Level Switch | Indicates bunker #1 is high and the conveyor must be stopped immediately. |  |
| B2HLP | Level Switch | Bunker 2 High Level Switch | Indicates bunker #2 is high and the conveyor must be stopped immediately. |  |
| B3FLP | Level Switch | Bunker 3 Full Level Switch | Indicates bunker #3 is full and can be shut down normally. |  |
| B3HLP | Level Switch | Bunker 3 High Level Switch | Indicates bunker #3 is high and the conveyor must be stopped immediately. |  |
| B3LLP | Level Switch | Bunker 3 Low Level Switch | Indicates bunker #3 is low. |  |
| BEM | Conveyor | Bucket Elevator | Conveys coal from the vibrating feeders to a point over diverter gate #1. | Cannot be started if diverter gate #1 diverting to conveyor #1 and conveyor #1 not running or gate #1 diverting to reclaim and reclaim is full. |
| BEP1 | Plug switch | Bucket Elevator Plug Switch | Indicates coal is piling up at bottom of bucket elevator |  |
| BEP2 | Plug switch | Bucket Elevator Plug Switch | Indicates coal is piling up at top of diverter gate #1. |  |
| BEZS | Speed switch | Bucket Elevator Speed Switch | Indicates that BE running |  |
| C1 | Conveyor | Conveyor #1 | Moves coal from diverter gate #1 to a point over diverter gate #2. | Cannot be started if diverter gate #2 diverting to conveyor #2 and conveyor #2 not running or gate #2 diverting to bunker #1 and bunker #1 full. |
| C1BA1 | AlignmentSwitch | C1 Belt Alignment Switch 1 | Indicates that conveyor belt out of alignment |  |
| C1BA2 | AlignmentSwitch | C1 Belt Alignment Switch 2 | Indicates that conveyor belt out of alignment |  |
| C1ES | E-Stop Pull Switch | C1 E-Stop Pull Cord | Indicates someone at the conveyor has requested an immediate stop |  |
| C1ZS | Speed switch | Conveyor #1 Speed Switch | Indicates that conveyor 1 is running |  |
| C2 | Conveyor | Conveyor #2 | Moves coal from diverter gate #2 to a point over diverter gate #3. | Cannot be started if diverter gate #3 diverting to conveyor #3 and conveyor #3 not running or gate #3 diverting to bunker #2 and bunker #2 full. |
| C2BA1 | AlignmentSwitch | C2 Belt Alignment Switch 1 | Indicates that conveyor belt out of alignment |  |
| C2BA2 | AlignmentSwitch | C2 Belt Alignment Switch 2 | Indicates that conveyor belt out of alignment |  |
| C2ES | E-Stop Pull Switch | C2 E-Stop Pull Cord | Indicates someone at the conveyor has requested an immediate stop |  |
| C2ZS | Speed switch | Conveyor #2 Speed Switch | Indicates that conveyor 2 is running |  |
| C3 | Conveyor | Conveyor #3 | Conveys coal from diverter gate #3 to bunker #3. | Cannot be started if bunker #3 full. |
| C3BA1 | AlignmentSwitch | C3 Belt Alignment Switch 1 | Indicates that conveyor belt out of alignment |  |
| C3BA2 | AlignmentSwitch | C3 Belt Alignment Switch 2 | Indicates that conveyor belt out of alignment |  |
| C3ES | E-Stop Pull Switch | C3 E-Stop Pull Cord | Indicates someone at the conveyor has requested an immediate stop |  |
| C3ZS | Speed switch | Conveyor #3 Speed Switch | Indicates that conveyor 3 is running |  |
| G1C1 | Limit Switch | Diverter Gate #1 switch | Indicates gate #1 in position to divert coal to conveyor 1 |  |
| G1C1R | Gate Control | Diverter Gate #1 Cylinder Control | Changes gate #1 to divert to conveyor 1 |  |
| G1LW | Limit Switch | Diverter Gate #1 Switch | Indicates gate #1 in position to divert coal to lowering well |  |
| G1LWR | Gate Control | Diverter Gate #1 Cylinder Control | Changes gate #1 to divert to lowering well |  |
| G2B1 | Limit Switch | Diverter Gate #2 Switch | Indicates gate #1 in position to divert coal to bunker 1 |  |
| G2B1R | Gate Control | Diverter Gate #2 Cylinder Control | Changes gate 2 to divert to bunker 1 |  |
| G2C2 | Limit Switch | Diverter Gate #2 Switch | Indicates gate #2 in position to divert coal to conveyor 2. |  |
| G2C2R | Gate Control | Diverter Gate #2 Cylinder Control | Changes gate 2 to divert to conveyor 2 |  |
| G2P | Plug Switch | Diverter Gate #2 plug switch | Indicates coal is piling above gate #2 |  |
| G3B2 | Limit Switch | Diverter Gate #3 Switch | Indicates gate #3 in position to divert coal to bunker 2 |  |
| G3B2R | Gate Control | Diverter Gate #3 Cylinder Control | Changes gate 3 to divert to bunker 2 |  |
| G3C3 | Limit Switch | Diverter Gate #3 Switch | Indicates gate #3 in position to divert coal to conveyor 3. |  |
| G3C3R | Gate Control | Diverter Gate #3 Cylinder Control | Changes gate 3 to divert to conveyor 3 |  |
| G3P | Plug Switch | Diverter Gate #3 plug switch | Indicates coal is piling above gate #3 |  |
| LWHLP | Level Switch | Lowering Well High Level Switch | Indicates that lowering well full |  |
| RFM | Motor | Reclaim Vibratory Feeder | Conveys coal from reclaim hopper to bucket elevator. | Cannot be started if bucket elevator not running. |
| UFM | Motor | Unloading Vibratory Feeder | Conveys coal from unloading hopper to bucket elevator. | Cannot be started if bucket elevator not running. |

# Operator Controls

Conveyor Controls On the operator control panel, a start/stop rotary switch is provided for each conveyor. The rotary switch has three positions, spring-return to the center. Twisting the switch clockwise closes that start contact. Twisting the switch counterclockwise opens the stop contact. A red indicator light is placed above the rotary switch and illuminates when the speed switch for the conveyor is on, indicating the conveyor is running.

Near each conveyor motor, a local control rotary switch is provided. The switch has three positions (Jog-Off-Rem), spring return from the counterclockwise position. In the center position, the conveyor is stopped and cannot run. When held in the counterclockwise position, the conveyor runs. In the clockwise position, the conveyor is controlled by the operator at the control panel, or automatically by the PLC if the system is in the auto operation mode.

Bucket Elevator Controls On the operator control panel, a start/stop rotary switch is provided for the bucket elevator. The rotary switch has three positions, spring-return to the center. Twisting the switch clockwise closes that start contact. Twisting the switch counterclockwise opens the stop contact. A red indicator light is placed above the rotary switch and illuminates when the speed switch for the bucket elevator is on, indicating the conveyor is running.

Near the top and bottom of the bucket elevator, a local control rotary switch is provided. Each switch has three positions (Jog-Off-Rem), spring return from the counterclockwise position. If either switch is in the center position, the conveyor is stopped and can only run if either switch is in the "Jog" position. When both switches are in the clockwise ("Rem") position, the conveyor is controlled by the operator at the control panel, or automatically by the PLC if the system is in the auto operation mode.

Feeder Controls On the operator control panel, a start/stop rotary switch is provided for each feeder. The rotary switch has three positions, spring-return to the center. Twisting the switch clockwise closes that start contact. Twisting the switch counterclockwise opens the stop contact. A red indicator light is placed above the rotary switch and illuminates when the auxiliary contact for the feeder motor is closed, indicating the feeder is running.

Near each feeder motor, a local control rotary switch is provided. The switch has three positions (Jog-Off-Rem), spring return from the counterclockwise position. In the center position, the feeder is stopped and cannot run. When held in the counterclockwise position, the feeder runs. In the clockwise position, the feeder is controlled by the operator at the control panel, or automatically by the PLC if the system is in the auto operation mode.

Diverter Gate Controls On the operator control panel, a rotary switch is provided for each gate position. The rotary switch has three positions, spring-return to the center. Twisting the switch clockwise causes the gate to move to divert coal to the right. Twisting the switch clockwise causes the gate to move to divert coal to the left. A white indicator light above and to the right of the rotary switch illuminates when the coal is diverted to go right. A white indicator light above and to the left of the rotary switch illuminates when the coal is diverted to go left.

Near each gate motor, a local control rotary switch and two pushbutton switches are provided. The rotary switch has three positions (Jog-Off-Rem), spring return from the counterclockwise position. In the center position, the gate cannot change positions. When held in the counterclockwise position, the gate position is commanded by the pushbuttons. There is a pushbutton for each diverter directions. In the clockwise position, the gate is controlled at the control panel.

Emergency Stop The operator control panel has an emergency-stop push-button switch. When pushed, all motors are immediately stopped. The button must be pulled to reset. The center part of the mushroom head has a red indicator that is illuminated as long as the button is "in."

Plug Indicators The operator control panel has an indicator for each plug that can be detected in the system.

System Status Indicators There are two system status indicators on the panel, "Ready" and "Purging." The Ready indicator is lit when E-stop is not active, all devices along a selected path have their local switches in the "remote" position, the safety switch is closed, and there is no plug. The specific conditions are listed below. The Purging indicator is lit while a purging operation is taking place.

If the unloading feeder is selected, its local control switch must be in the "remote" position and its safety switch must be closed.

If the reclaim feeder is selected, its local control switch must be in the "remote" position and its safety switch must be closed.

AND

The bucket elevator local control switch must be in the "remote" position, its safety switch must be closed, and both plug switches must be closed (no plug).

AND

The gate 1 local control switch must be in the "remote" position and its safety switch must be closed.

If gate 1 is in the "lowering well" position, plug switch must closed (no plug) and the reclaim pile not high.

If gate 1 is in the "conveyor 1" position, plug switch must closed (no plug) and the reclaim pile not high.

System Auto Control The operator panel has a three-position rotary switch, spring-return to the center. Twisting the switch clockwise causes the conveyors in the selected path to start in reverse order, then start the bucket elevator, then start the selected feeder. Twisting the switch clockwise starts a purge operation where the source feeder is immediately stopped, the bucket elevator is stopped after a minute delay and then the conveyors in the selected path are stopped after appropriate delays to allow the coal to cleared from the conveyor.

Operation Mode The operator panel has a three position rotary switch. All three positions are maintained. In the middle "OFF" position, the system cannot be controlled from the operator panel. The devices must be controlled with the local control switches. In the clockwise, "MAN," position, the conveyors, bucket elevator, and feeders are started/stopped from the operator panel controls. In the counterclockwise, "AUTO," position, the System Auto Control switch is used to start/stop the appropriate conveyors and feeders depending on the selected gate positions.

Source Feeder The operator panel has a two-position rotary switch that selects the source feeder. This switch selects the source feeder in both manual and automatic operation modes. In the clockwise position, labeled "RECL," only the reclaim feeder can be started to feed the bucket elevator. In the counterclockwise position, labeled "UNL," only the unloading feeder can be started to feed the bucket elevator.

Warning Horns The operator panel has a two-position rotary switch that the operator uses to sound the warning horns before starting conveyors. It is operational only in the manual operation mode. Its normal position is counterclockwise, spring-return to this position. When rotated clockwise, the warning horn at the elevator pit (horn #1) and gate 1 (horn #2) is sounded. If diverter gate #2 is selected to divert coal to conveyor #2, then the horn at gate 2 (horn #3) is sounded. If diverter gate #3 is selected to divert coal to conveyor #3, then the horn at gate 3 (horn #4) is sounded.

# Local Operation

A local station at each major piece of equipment (feeders, bucket elevator, gates, and conveyors) provides local jog operation for maintenance and test. Local operation should not be used to move coal from a source feeder to a destination bunker. The person must rotate the Jog-Off-Remote selector switch to the Jog position and hold it there to run the equipment (the switch is spring-loaded to return move the switch from the Jog to the Off position. For the diverter gates, the operator must hold the Jog-Off-Remote switch in the Jog position and also press a pushbutton to move the gate to the desired position.

The following interlocks will prevent equipment operation in local jog operation:

- System E-Stop switch pulled out

- Local safety switch disconnected

- Pull-cord E-stop (conveyors)

Equipment interlock is not provided. The switch at the local station must be in the "Remote" position for the manual and automatic operation modes.

# Manual Mode Operation

Using the control panel close to boiler #3, the operator individually sets the diverter gate positions and then individually starts the conveyors, bucket elevator, and feeder. The Operation Mode switch must be in the "MAN" position. In addition, all local station switches must be in the "Remote" position for the manual operation mode.

The operator first sets the diverter gate positions and the desired source feeder to determine the path between the source and destination. Interlocks in the system prevent operation of the system if a problem exists. The operator should do the following procedure:

- Select "MAN" Operation Mode switch position

- Check OI panel for annunciators and alarm conditions. Acknowledge any alarms and clear any conditions.

- Place the diverter gates in the proper positions

- Select the proper source feeder: "UNL" for unloading hopper; "RECL" for reclaim hopper.

- When the route is proper and all safety devices are in the proper position, the "READY" indicator will be lit.

- Activate the Start for the last conveyor in the path. Hold the Start for a few seconds until the Run light illuminates.

- Repeat step 6 for each conveyor (or bucket elevator) in the path.

- Lastly, start the appropriate feeder.

Interlocks prevent the operator from starting in the wrong order. If a fault occurs during operation, the affected device and all devices upstream from the device will be immediately stopped. Downstream conveyors will remain running.

The system is shut down in one of the following ways:

- Move the System Auto Control switch to the "Purge/Stop" position. The source feeder is immediately stopped. After appropriate delays (detailed in the automatic mode operation section) the equipment is shut off after allowing time for coal to be cleared.

- When the destination bunker is full, an automatic purge is initiated.

- Activate the Stop switch for the source feeder and then the bucket elevator and then the conveyors. Allow appropriate time to allow coal to be cleared from the elevator/conveyor before shutting it off. This delay is very important for the bucket elevator. Material left on the elevator will cause it to run backward and may damage the elevator.

- Activate the Stop switch for the last conveyor in the path. This method is not recommended since it will cause an immediate stop of all equipment in the path. Material left on the bucket elevator will cause it to run backward and may damage the elevator.

# Automatic Mode Operation

The operator individually sets the diverter gate positions to establish the source-to-destination path. When the operator initiates a start (System Auto Control switch), the conveyors, bucket elevator, and appropriate feeders are started in the appropriate order. When the operator initiates a purge/stop (System Auto Control switch), the conveyors, bucket elevator, and appropriate feeders are stopped in the appropriate order with an intervening delay to allow material to be cleared from the equipment. Also, when the destination bunker is low (currently only bunker 3 has a low sensor) and the path to bunker 3 is selected, an automatic start is initiated. When the destination bunker is full (currently only bunker 3), an automatic purge is initiated.

The Operation Mode switch must be in the "AUTO" position. In addition, all local station switches must be in the "Remote" position for the manual operation mode.

The operator first sets the diverter gate positions and the desired source feeder to determine the path between the source and destination. Interlocks in the system prevent operation of the system if a problem exists. The operator should do the following procedure:

- Select "MAN" Operation Mode switch position

- Check OI panel for annunciators and alarm conditions. Acknowledge any alarms and clear any conditions.

- Place the diverter gates in the proper positions

- Select the proper source feeder: "UNL" for unloading hopper; "RECL" for reclaim hopper.

- Select "AUTO" Operation Mode switch position

- When the route is proper and all safety devices are in the proper position, the "READY" indicator will be lit.

- Activate the "Start/Restart" switch. The conveyors will start in reverse order and lastly the appropriate feeder starts. Details are below.

The system is shut down by moving the System Auto Control switch to the "Purge/Stop" position. The source feeder is immediately stopped. After appropriate delays (detailed below) the equipment is shut off after allowing time for coal to be cleared.

Interlocks prevent the operator from starting in the wrong order. If a fault occurs during operation, the affected device and all devices upstream from the device will be immediately stopped. Downstream conveyors will remain running.

Detailed Procedures:

	Start/Restart – Starts transfer of coal to the bunker indicated by the gate positions. Do not allow this operation to start if not in Auto mode. Steps:

If G1 diverts to C1 and G2 diverts to C2 and G3 diverts to C3

Start C3

If G1 diverts to C1 and G2 diverts to C2

Start C2

If G1 diverts to C1

Start C1

Start BE

If reclaim selected

Start RF

Else

Start UF

	Purge/Stop – Purges conveyors of coal, stopping them after allowing time for each conveyor to clear of coal. Do not allow this operation to start if not in Auto mode. Steps:

If reclaim selected

Stop RF

Else

Stop UF

Wait 1 minute

Stop BE

If G1 diverts to C1

Wait 1 minute

Stop C1

If G2 diverts to C2

Wait 1 minute

Stop C2

If G3 diverts to C3

Wait 30 seconds

Start C3

# Device Operation

## Unloading Feeder

The unloading feeder conveys coal from the unloading hopper to the bucket elevator.

Process System Items

Motor Starter (contactor driving a SCR control)

Jog-Off-Remote (UFJS) local control

Start/Stop at operator control panel

Safety cut-off switch (UFSS)

Auxiliary contact (UFS)

Detail Design:

Physical Inputs:

UFS - Auxiliary contact (on when feeder running)

UFSS - Safety cut-off contact (on when safety switch closed)

Physical Outputs:

UFR - Starter (on to start/run feeder)

Local Commands:

UFJSJ - On when Jog-Off-Remote switch in Jog position

UFJSR - On when Jog-Off-Remote switch in Remote position

Operator Commands:

UFSTPS - Operator stop contact (off when operator commanding stop)

UFSTS - Operator start contact (on when operator commanding start)

UFSR - On when unloading feeder selected as source by operator

Operator Indications:

Run status (same as auxiliary contact)

Local selector alarm (on when alarm)

Safety switch alarm (on when alarm)

Implementation: UFSS must be closed and E-Stop not active for this device to run. When the Jog-Off-Remote switch is in the jog position, the feeder runs. The Jog-Off-Remote switch must be in the remote position for the feeder to be controlled in either manual or automatic mode. The unloading feeder must be selected and the bucket elevator running before this feeder can be started in manual and automatic operation modes. In automatic mode, this feeder (if selected as the source) is the first device stopped when purging. In automatic mode, this feeder (if selected as the source) is started after the bucket elevator is running. The start and stop contacts are momentary. If in automatic operation, the operator can immediately stop the feeder with the stop contact.

The local selector alarm is on if the local selector switch for the feeder is not in the "Remote" position. The safety switch alarm is on if the local safety switch for the feeder is open.

## Reclaim Feeder

The reclaim feeder conveys coal from the hopper below the reclaim coal pile to the bucket elevator.

Process System Items

Motor Starter (contactor driving a SCR control)

Jog-Off-Remote (RFJS) local control

Start/Stop at operator control panel

Safety cut-off switch (RFSS)

Auxiliary contact (RFS)

Detail Design:

Physical Inputs:

RFS - Auxiliary contact (on when feeder running)

RFSS - Safety cut-off contact (on when safety switch closed)

Physical Outputs:

RFR - Starter (on to start/run feeder)

Local Commands:

RFJSJ - On when Jog-Off-Remote switch in Jog position

RFJSR - On when Jog-Off-Remote switch in Remote position

Operator Commands:

RFSTPS - Operator stop contact (off when operator commanding stop)

RFSTS - Operator start contact (on when operator commanding start)

RFSR - On when unloading feeder selected as source by operator

Operator Indications:

Run status (same as auxiliary contact)

Local selector alarm (on when alarm)

Safety switch alarm (on when alarm)

Implementation: RFSS must be closed and E-Stop not active for this device to run. When the Jog-Off-Remote switch is in the jog position, the feeder runs. The Jog-Off-Remote switch must be in the remote position for the feeder to be controlled in either manual or automatic mode. The reclaim feeder must be selected and the bucket elevator running before this feeder can be started in manual and automatic operation modes. In automatic mode, this feeder (if selected as the source) is the first device stopped when purging. In automatic mode, this feeder (if selected as the source) is started after the bucket elevator is running. The start and stop contacts are momentary. If in automatic operation, the operator can immediately stop the feeder with the stop contact.

The local selector alarm is on if the local selector switch for the feeder is not in the "Remote" position. The safety switch alarm is on if the local safety switch for the feeder is open.

## Bucket Elevator

The bucket elevator conveys coal from either vibratory feeder to the chute above gate 1.

Process System Items

Motor Starter (contactor)

Jog-Off-Remote (BEJS1) local control at bottom of elevator

Jog-Off-Remote (BEJS2) local control at top of elevator

Start/Stop at operator control panel

Safety cut-off switch (BESS)

Speed switch (BEZS)

Plug switch at bottom (BEP1)

Plug switch at top (BEP2)

Plug switch in chute to lowering well (G1LWP)

Lowering well high switch (LWHLP)

Detail Design:

Physical Inputs:

BESS - Safety cut-off contact (on when safety switch closed)

BEZS - Speed contact (on when elevator running)

BEP1 - Plug contact (off when coal plugged at bottom of elevator)

BEP2 - Plug contact (off when coal plugged at top of elevator)

G1LWP - Plug contact (off when coal plugged in chute to lowering well)

LWHLP - Lowering well high level (off when high level)

Physical Outputs:

BER - Starter (on to start/run bucket elevator)

Local Commands:

BEJS1J - On when Jog-Off-Remote switch 1 in Jog position

BEJS1R - On when Jog-Off-Remote switch 1 in Remote position

BEJS2J - On when Jog-Off-Remote switch 2 in Jog position

BEJS2R - On when Jog-Off-Remote switch 2 in Remote position

Operator Commands:

BESTPS - Operator stop contact (off when operator commanding stop)

BESTS - Operator start contact (on when operator commanding start)

Operator Indications:

Run status (same as zero speed switch)

Local selector alarm (on when alarm)

Safety switch alarm (on when alarm)

Zero-speed alarm (off when alarm)

Plug 1 alarm (on when alarm)

Plug 2 alarm (on when alarm)

Implementation: BESS must be closed and E-Stop not active for this device to run. When either Jog-Off-Remote switch is in the jog position, the bucket elevator runs. Both Jog-Off-Remote switches must be in the remote position for the elevator to be controlled in either manual or automatic mode. If gate 1 is diverting coal to conveyor 1, conveyor 1 must be running before the bucket elevator can be started in manual and automatic operation modes. In automatic mode, the bucket elevator is stopped 1 minute seconds after the selected feeder is stopped when purging. In automatic mode, the bucket elevator is started first if gate 1 is diverting coal to the lowering well. Otherwise, it starts after conveyor 1 is running. The start and stop contacts are momentary. If in automatic operation, the operator can immediately stop the bucket elevator with the stop contact.

When either BEP1 or BEP2 indicates a plug, the elevator is immediately stopped. If gate 1 is diverting to the lowering well, when G1LWP indicates a plug or the lowering well level is high, the elevator is immediately stopped.

The local selector alarm is on if either local selector switch for the bucket elevator is not in the "Remote" position. The safety switch alarm is on if the local safety switch for the bucket elevator is open. The zero speed alarm is on if the zero speed switch indicates zero speed when the conveyor motor is running. This alarm is suppressed for 6 seconds when starting the bucket elevator. The plug alarms are set when the plug indicator is off for 3 seconds.

## Diverter Gate 1

Diverter gate 1 diverts coal to either the lowering well or to conveyor 1.

Process System Items

Pneumatic cylinder control (valve)

Jog-Off-Remote (G1JS) local control

LW/C1 pushbutton local control

LW/C1 selection at operator control panel

Safety cut-off switch (G1SS)

Gate in LW divert position (G1LW)

Gate in C1 divert position (G1C1)

Plug switch in chute to lowering well (G1LWP)

Detail Design:

Physical Inputs:

G1SS - Safety cut-off contact (on when safety switch closed)

G1LW - Gate in position to divert to lowering well (on when in this position)

G1C1 - Gate in position to divert to conveyor 1 (on when in this position)

G1LWP - Plug contact (off when coal plugged in chute to lowering well)

Physical Outputs:

GLWRR - G1 to LW control (on to change gate to divert to lowering well)

G1C1RR - G1 to C1 control (on to change gate to divert to conveyor 1)

Local Commands:

G1LWS - On when Jog-Off-Remote switch in Jog position and local request to move to divert to lowering well

G1C1S - On when Jog-Off-Remote switch in Jog position and local request to move to divert to conveyor 1

G1JSR - On when Jog-Off-Remote switch in Remote position

Operator Commands:

G1LWPS - Operator panel contact (on when requesting divert to lowering well)

G1C1PS - Operator panel contact (on when requesting divert to conveyor 1)

Operator Indications:

Gate 1 in lowering well position

Gate 1 in conveyor 1 position

Plug in chute to lowering well alarm (on when alarm)

Implementation: G1SS must be closed and E-Stop not active for the gate position to change. When the Jog-Off-Remote switch is in the jog position, the LW pushbutton at the local station must be pressed to change the gate to divert to the lowering well and the C1 pushbutton at the local station must be pressed to change the gate to divert to conveyor 1. When the Jog-Off-Remote switch is the remote position and the operation mode is manual, the gate position is commanded from the operator panel.

The plug alarm is set when the plug indicator is off for 3 seconds.

## Conveyor 1

Conveyor 1 moves coal from gate 1 to either bunker 1 or to conveyor 2.

Process System Items

Motor Starter (contactor)

Jog-Off-Remote (C1JS) local control

Start/Stop at operator control panel

Safety cut-off switch (C1SS)

Speed switch (C1ZS)

Belt alignment switch (C1BA2)

Plug switch at bunker 1 (G2B1P)

Plug switch at gate 2 (G2P)

Bunker 1 full (B1FLP)

Detail Design:

Physical Inputs:

C1SS - Safety cut-off contact (on when safety switch closed)

C1ZS - Speed contact (on when elevator running)

C1BA2 - Belt alignment switch (off when belt mis-aligned)

G2B1P - Plug contact (off when coal plugged to bunker 1)

G2P - Plug contact (off when coal plugged to gate 2)

B1FLP - Bunker 1 full (off when full)

Physical Outputs:

C1R - Starter (on to start/run conveyor 1)

Local Commands:

C1JSJ - On when Jog-Off-Remote switch in Jog position

C1JSR - On when Jog-Off-Remote switch in Remote position

Operator Commands:

C1STPS - Operator stop contact (off when operator commanding stop)

C1STS - Operator start contact (on when operator commanding start)

Operator Indications:

Run status (same as zero speed switch)

Local selector alarm (on when alarm)

Safety switch alarm (on when alarm)

Belt alignment alarm (on when alarm)

Zero-speed alarm (off when alarm)

Pull-cord E-stop alarm (on when alarm)

Implementation: C1SS must be closed and E-Stop not active for this device to run. When the Jog-Off-Remote switch is in the jog position, the conveyor runs. The Jog-Off-Remote switch must be in the remote position for the conveyor to be controlled in either manual or automatic mode. If gate 2 is diverting coal to conveyor 2, conveyor 2 must be running before conveyor 1 can be started in manual and automatic operation modes. In automatic mode and with gate 1 diverting to conveyor 1, conveyor 1 is stopped 1 minute after the bucket elevator is stopped when purging. In automatic mode, conveyor 1 is started after the bucket elevator is running if gate 1 is diverting coal to conveyor 1. The start and stop contacts are momentary. If in automatic operation, the operator can immediately stop the conveyor with the stop contact.

In the automatic and manual modes, when G2P indicates a plug or either belt alignment switch indicates a belt problem, the conveyor is immediately stopped. If gate 2 is diverting to bunker 1, when G2B1P indicates a plug, the conveyor is immediately stopped.

In the automatic mode, if the path is selected to bunker 1, when bunker 1 is full, the conveyors are purged.

The local selector alarm is on if either local selector switch for the conveyor is not in the "Remote" position. The safety switch alarm is on if the local safety switch for the conveyor is open. The zero speed alarm is on if the zero speed switch indicates zero speed when the conveyor motor is running. This alarm is suppressed for 6 seconds when starting the conveyor. The belt alignment alarm is on if either belt alignment switch for conveyor 1 has been open for 1 second, indicating a problem with the belt. The pull-cord E-stop alarm is on if the conveyor pull-cord has been pulled.

## Diverter Gate 2

Diverter gate 2 diverts coal to either bunker 1 or to conveyor 2.

Process System Items

Pneumatic cylinder control (valve)

Jog-Off-Remote (G2JS) local control

B1/C2 pushbutton local control

B1/C2 selection at operator control panel

Safety cut-off switch (G2SS)

Gate in bunker 1 divert position (G2B1)

Gate in C2 divert position (G2C2)

Plug switch at bunker 1 (G2B1P)

Plug switch at gate 2 (G2P)

Detail Design:

Physical Inputs:

G2SS - Safety cut-off contact (on when safety switch closed)

G2B1 - Gate in position to divert to bunker 1 (on when in this position)

G2C2 - Gate in position to divert to conveyor 2 (on when in this position)

G2B1P - Plug contact (off when coal plugged to bunker 1)

G2P - Plug contact (off when coal plugged to gate 2)

Physical Outputs:

G2B1RR - G2 to bunker 1 control (on to change gate to divert to bunker 1)

G2C2RR - G2 to C2 control (on to change gate to divert to conveyor 2)

Local Commands:

G2B1S - On when Jog-Off-Remote switch in Jog position and local request to move to divert to bunker 1

G2C2S - On when Jog-Off-Remote switch in Jog position and local request to move to divert to conveyor 2

G2JSR - On when Jog-Off-Remote switch in Remote position

Operator Commands:

G2B1PS - Operator panel contact (on when requesting divert to bunker 1)

G2C2PS - Operator panel contact (on when requesting divert to conveyor 2)

Operator Indications:

Gate 2 in bunker 1 position

Gate 2 in conveyor 2 position

Implementation: G2SS must be closed and E-Stop not active for the gate position to change. When the Jog-Off-Remote switch is in the jog position, the B1 pushbutton at the local station must be pressed to change the gate to divert to bunker 1 and the C2 pushbutton at the local station must be pressed to change the gate to divert to conveyor 2. When the Jog-Off-Remote switch is the remote position and the operation mode is manual, the gate position is commanded from the operator panel.

The plug alarms are set when the plug indicator is off for 3 seconds.

## Conveyor 2

Conveyor 2 moves coal from gate 2 to either bunker 2 or to conveyor 3.

Process System Items

Motor Starter (contactor)

Jog-Off-Remote (C2JS) local control

Start/Stop at operator control panel

Safety cut-off switch (C2SS)

Speed switch (C2ZS)

Belt alignment switch (C2BA2)

Plug switch at bunker 2 (G3B2P)

Plug switch at gate 3 (G3P)

Bunker 2 full (B2FLP)

Detail Design:

Physical Inputs:

C2SS - Safety cut-off contact (on when safety switch closed)

C2ZS - Speed contact (on when elevator running)

C2BA2 - Belt alignment switch (off when belt mis-aligned)

G3B2P - Plug contact (off when coal plugged to bunker 2)

G3P - Plug contact (off when coal plugged to gate 3)

B1FLP - Bunker 1 full (off when full)

Physical Outputs:

C2R - Starter (on to start/run conveyor 2)

Local Commands:

C2JSJ - On when Jog-Off-Remote switch in Jog position

C2JSR - On when Jog-Off-Remote switch in Remote position

Operator Commands:

C2STPS - Operator stop contact (off when operator commanding stop)

C2STS - Operator start contact (on when operator commanding start)

Operator Indications:

Run status (same as zero speed switch)

Local selector alarm (on when alarm)

Safety switch alarm (on when alarm)

Belt alignment alarm (on when alarm)

Zero-speed alarm (off when alarm)

Pull-cord E-stop alarm (on when alarm)

Implementation: C2SS must be closed and E-Stop not active for this device to run. When the Jog-Off-Remote switch is in the jog position, the conveyor runs. The Jog-Off-Remote switch must be in the remote position for the conveyor to be controlled in either manual or automatic mode. If gate 3 is diverting coal to conveyor 3, conveyor 3 must be running before conveyor 2 can be started in manual and automatic operation modes. In automatic mode and with gate 2 diverting to conveyor 2, conveyor 2 is stopped 1 mnute after conveyor 1 is stopped when purging. In automatic mode, conveyor 2 is started after conveyor 1 is running if gate 2 is diverting coal to conveyor 2. The start and stop contacts are momentary. If in automatic operation, the operator can immediately stop the conveyor with the stop contact.

In the automatic and manual modes, when G3P indicates a plug or either belt alignment switch indicates a belt problem, the conveyor is immediately stopped. If gate 3 is diverting to bunker 2, when G3B2P indicates a plug, the conveyor is immediately stopped.

In the automatic mode, if the path is selected to bunker 2, when bunker 2 is full, the conveyors are purged.

The local selector alarm is on if either local selector switch for the conveyor is not in the "Remote" position. The safety switch alarm is on if the local safety switch for the conveyor is open. The zero speed alarm is on if the zero speed switch indicates zero speed when the conveyor motor is running. This alarm is suppressed for 6 seconds when starting the conveyor. The belt alignment alarm is on if either belt alignment switch for conveyor 1 has been open for 1 second, indicating a problem with the belt. The pull-cord E-stop alarm is on if the conveyor pull-cord has been pulled.

## Diverter Gate 3

Diverter gate 3 diverts coal to either bunker 2 or to conveyor 3.

Process System Items

Pneumatic cylinder control (valve)

Jog-Off-Remote (G3JS) local control

B2/C3 pushbutton local control

B2/C3 selection at operator control panel

Safety cut-off switch (G3SS)

Gate in bunker 1 divert position (G3B2)

Gate in C2 divert position (G3C3)

Plug switch at bunker 2 (G3B2P)

Plug switch at gate 3 (G3P)

Detail Design:

Physical Inputs:

G3SS - Safety cut-off contact (on when safety switch closed)

G3B2 - Gate in position to divert to bunker 2 (on when in this position)

G3C3 - Gate in position to divert to conveyor 3 (on when in this position)

G3B2P - Plug contact (off when coal plugged to bunker 2)

G3P - Plug contact (off when coal plugged to gate 3)

Physical Outputs:

G3B2RR - G3 to bunker 2 control (on to change gate to divert to bunker 2)

G3C3RR - G3 to C3 control (on to change gate to divert to conveyor 3)

Local Commands:

G3B2S - On when Jog-Off-Remote switch in Jog position and local request to move to divert to bunker 2

G3C3S - On when Jog-Off-Remote switch in Jog position and local request to move to divert to conveyor 3

G3JSR - On when Jog-Off-Remote switch in Remote position

Operator Commands:

G3B2PS - Operator panel contact (on when requesting divert to bunker 2)

G3C3PS - Operator panel contact (on when requesting divert to conveyor 3)

Operator Indications:

Gate 3 in bunker 2 position

Gate 3 in conveyor 3 position

Implementation: G3SS must be closed and E-Stop not active for the gate position to change. When the Jog-Off-Remote switch is in the jog position, the B2 pushbutton at the local station must be pressed to change the gate to divert to bunker 2 and the C3 pushbutton at the local station must be pressed to change the gate to divert to conveyor 3. When the Jog-Off-Remote switch is the remote position and the operation mode is manual, the gate position is commanded from the operator panel.

The plug alarms are set when the plug indicator is off for 3 seconds.

## Conveyor 3

Conveyor 3 moves coal from gate 3 to bunker 3.

Process System Items

Motor Starter (contactor)

Jog-Off-Remote (C3JS) local control

Start/Stop at operator control panel

Safety cut-off switch (C3SS)

Speed switch (C3ZS)

Belt alignment switch (C3BA2)

Bunker 3 full (B3FLP)

Bunker 3 low (B3LLP)

Detail Design:

Physical Inputs:

C3SS - Safety cut-off contact (on when safety switch closed)

C3ZS - Speed contact (on when elevator running)

C3BA2 - Belt alignment switch (off when belt mis-aligned)

B3FLP - Bunker 3 full contact (off when full)

B3LLP - Bunker 3 low contact (off when low)

Physical Outputs:

C3R - Starter (on to start/run conveyor 3)

Local Commands:

C3JSJ - On when Jog-Off-Remote switch in Jog position

C3JSR - On when Jog-Off-Remote switch in Remote position

Operator Commands:

C3STPS - Operator stop contact (off when operator commanding stop)

C3STS - Operator start contact (on when operator commanding start)

Operator Indications:

Run status (same as zero speed switch)

Local selector alarm (on when alarm)

Safety switch alarm (on when alarm)

Belt alignment alarm (on when alarm)

Zero-speed alarm (off when alarm)

Pull-cord E-stop alarm (on when alarm)

Implementation: C3SS must be closed and E-Stop not active for this device to run. When the Jog-Off-Remote switch is in the jog position, the conveyor runs. The Jog-Off-Remote switch must be in the remote position for the conveyor to be controlled in either manual or automatic mode. In automatic mode and with gate 3 diverting to conveyor 3, conveyor 3 is stopped 30 seconds after conveyor 2 is stopped when purging. In automatic mode, this conveyor is started first if gate 3 is diverting coal to conveyor 3. The start and stop contacts are momentary. If in automatic operation, the operator can immediately stop the conveyor with the stop contact.

In the automatic and manual modes, when either belt alignment switch indicates a belt problem, the conveyor is immediately stopped.

In the automatic mode, if the path is selected to bunker 3, and bunker 3 is low, the conveyors are started automatically to convey coal to bunker 3. When bunker 3 is full, the conveyors are purged.

The local selector alarm is on if either local selector switch for the conveyor is not in the "Remote" position. The safety switch alarm is on if the local safety switch for the conveyor is open. The zero speed alarm is on if the zero speed switch indicates zero speed when the conveyor motor is running. This alarm is suppressed for 6 seconds when starting the conveyor. The belt alignment alarm is on if either belt alignment switch for conveyor 1 has been open for 1 second, indicating a problem with the belt. The pull-cord E-stop alarm is on if the conveyor pull-cord has been pulled.