- Coal Handler

- OI Panel Description

Note: This document describes the operation of a small operator panel. The mapping of the internal memory of the panel and the controller tags is not described, so this is not a complete description.

Table of Contents

OI Panel Overview	4

Main Screen	5

Conveyors/Gates Alarm Summary Screen	6

Conveyor 1 Alarm Screen	7

Conveyor 2 Alarm Screen	8

Conveyor 3 Alarm Screen	8

Gate 1 Alarm Screen	9

Gate 2 Alarm Screen	10

Gate 3 Alarm Screen	11

Equipment Alarm Summary Screen	12

Unloading Feeder Alarm Screen	13

Reclaim Feeder Alarm Screen	14

Bucket Elevator Alarm Screen	15

Lowering Well Alarm Screen	16

Temperature Alarm Screen	17

Bunker Levels Screen	18

Plug/Alignment Screen	19

Mapping Between SLC Memory and OI Panel Registers	20

Alarms Tracked in Alarm History	23

# OI Panel Overview

Alarms are annunciated and recorded on the OI Panel. The OI Panel is a touch screen. Pressing the button objects on the screens will perform an action, such as display another screen, or acknowledge an alarm. The operation of the various screens is described first, followed by a description of the mapping between the SLC-5/04 memory locations and the OI Panel registers. The alarms tracked by the alarm history are also described.

# Main Screen

CONVEYOR/GATE ALARMS button - Pressing this button will display the alarm summary for the conveyors and gates. This button is red if there are any alarms connected with the conveyors and gates. The button is flashing red if there are any unacknowledged conveyor/gate alarms.

EQUIPMENT ALARMS button - Pressing this button will display the alarm summary for the feeders, bucket elevator, lowering well, and temperature. This button is red if there are any alarms connected with these devices. The button is flashing red if there are any unacknowledged equipment alarms.

BUNKER LEVELS button - Pressing this button will display the state of the bunker level indicators.

PLUG/ALIGN INDIC button - Pressing this button will display the state of the plug and belt alignment indicators.

ALARM HISTORY button - Pressing this button will display the alarm history, a record of the last 99 alarms. The time the alarm occurred is recorded, along with the time the alarm cleared.

CLEAR ALARM HISTORY button - Pressing this button will clear all records from the alarm history.

# Conveyors/Gates Alarm Summary Screen

This screen summarizes the alarms for the gates and conveyors.

CONVEYOR 1 button - Pressing this button will display the alarms for conveyor 1. This button is red if there are any alarms connected with the conveyor. The button is flashing red if there are any unacknowledged alarms associated with conveyor 1.

CONVEYOR 2 button - Pressing this button will display the alarms for conveyor 2. This button is red if there are any alarms connected with the conveyor. The button is flashing red if there are any unacknowledged alarms associated with conveyor 2.

CONVEYOR 3 button - Pressing this button will display the alarms for conveyor 3. This button is red if there are any alarms connected with the conveyor. The button is flashing red if there are any unacknowledged alarms associated with conveyor 3.

GATE 1 button - Pressing this button will display the alarms for gate 1. This button is red if there are any alarms connected with the gate. The button is flashing red if there are any unacknowledged alarms associated with gate 1.

GATE 2 button - Pressing this button will display the alarms for gate 2. This button is red if there are any alarms connected with the gate. The button is flashing red if there are any unacknowledged alarms associated with gate 2.

GATE 3 button - Pressing this button will display the alarms for gate 3. This button is red if there are any alarms connected with the gate. The button is flashing red if there are any unacknowledged alarms associated with gate 3.

BACK TO START button - Pressing this button will display the main screen.

## Conveyor 1 Alarm Screen

LOCAL SELECTOR - Red if the local selector switch for conveyor 1 is not in the "Remote" position. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the local selector switch is in the "Remote" position.

SAFETY SWITCH - Red if the local safety switch for conveyor 1 is open. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the safety switch is closed.

BELT ALIGNMENT - Red if either belt alignment switch for conveyor 1 is open, indicating a problem with the belt. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when both belt alignment switches are closed.

ZERO SPEED - Red if the conveyor 1 zero speed switch indicates zero speed when the conveyor motor is running. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when there is no problem.

E-STOP PULL CORD - Red if the conveyor 1 pull cord has been pulled. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when there is no problem.

ACKNOWLEDGE ALARM button - Pressing this button will cause any flashing indicators on this display to stop flashing. If the alarm condition is no longer on, then it will not be red.

PREV SCREEN button - Pressing this button will display the conveyor/gate alarm summary screen.

BACK TO START button - Pressing this button will display the main screen.

## Conveyor 2 Alarm Screen

The indicators and controls are the same as for the Conveyor 1 alarm screen

## Conveyor 3 Alarm Screen

The indicators and controls are the same as for the Conveyor 1 alarm screen

## Gate 1 Alarm Screen

PLUG RELAY TO LOWERING WELL - Red if there is a coal plug in the chute leading to the lowering well. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when there is no plug.

PLUG RELAY - Alarm not functional. Intended to be used to indicate plug at top of gate, but sensor is not installed.

SAFETY SWITCH - Red if the local safety switch for gate 1 is open. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the safety switch is closed.

LOCAL SELECTOR - Red if the local selector switch for gate 1 is not in the "Remote" position. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the local selector switch is in the "Remote" position.

ACKNOWLEDGE ALARM button - Pressing this button will cause any flashing indicators on this display to stop flashing. If the alarm condition is no longer on, then it will not be red.

PREV SCREEN button - Pressing this button will display the conveyor/gate alarm summary screen.

BACK TO START button - Pressing this button will display the main screen.

## Gate 2 Alarm Screen

PLUG RELAY TO BUNKER 1 - Red if there is a coal plug in the chute leading to bunker 1. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when there is no plug.

PLUG RELAY - Red if there is a coal plug in the chute above the gate. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when there is no plug.

SAFETY SWITCH - Red if the local safety switch for gate 2 is open. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the safety switch is closed.

LOCAL SELECTOR - Red if the local selector switch for gate 2 is not in the "Remote" position. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the local selector switch is in the "Remote" position.

ACKNOWLEDGE ALARM button - Pressing this button will cause any flashing indicators on this display to stop flashing. If the alarm condition is no longer on, then it will not be red.

PREV SCREEN button - Pressing this button will display the conveyor/gate alarm summary screen.

BACK TO START button - Pressing this button will display the main screen.

## Gate 3 Alarm Screen

PLUG RELAY TO BUNKER 2 - Red if there is a coal plug in the chute leading to bunker 2. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when there is no plug.

PLUG RELAY - Red if there is a coal plug in the chute above the gate. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when there is no plug.

SAFETY SWITCH - Red if the local safety switch for gate 3 is open. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the safety switch is closed.

LOCAL SELECTOR - Red if the local selector switch for gate 3 is not in the "Remote" position. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the local selector switch is in the "Remote" position.

ACKNOWLEDGE ALARM button - Pressing this button will cause any flashing indicators on this display to stop flashing. If the alarm condition is no longer on, then it will not be red.

PREV SCREEN button - Pressing this button will display the conveyor/gate alarm summary screen.

BACK TO START button - Pressing this button will display the main screen.

# Equipment Alarm Summary Screen

This screen summarizes the alarms for the feeders, bucket elevator, lowering well, and temperature.

UNLOADING FEEDER button - Pressing this button will display the alarms for the unloading feeder. This button is red if there are any alarms connected with the feeder. The button is flashing red if there are any unacknowledged alarms associated with the unloading feeder.

BUCKET ELEVATOR button - Pressing this button will display the alarms for the bucket elevator. This button is red if there are any alarms connected with the bucket elevator. The button is flashing red if there are any unacknowledged alarms associated with the bucket elevator.

RECLAIM FEEDER button - Pressing this button will display the alarms for the reclaim feeder. This button is red if there are any alarms connected with the feeder. The button is flashing red if there are any unacknowledged alarms associated with the reclaim feeder.

LOWERING WELL button - Pressing this button will display the alarms for the lowering well. This button is red if there are any alarms connected with the lowering well. The button is flashing red if there are any unacknowledged alarms associated with the lowering well.

TEMPERATURE button - Pressing this button will display the temperature alarms. This button is red if there are any temperature alarms with the gate. The button is flashing red if there are any unacknowledged temperature alarms.

BACK TO START button - Pressing this button will display the main screen.

## Unloading Feeder Alarm Screen

LOCAL SELECTOR - Red if the local selector switch for the unloading feeder is not in the "Remote" position. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the local selector switch is in the "Remote" position.

SAFETY SWITCH - Red if the local safety switch for the unloading feeder is open. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the safety switch is closed.

ACKNOWLEDGE ALARM button - Pressing this button will cause any flashing indicators on this display to stop flashing. If the alarm condition is no longer on, then it will not be red.

PREV SCREEN button - Pressing this button will display the equipment alarm summary screen.

BACK TO START button - Pressing this button will display the main screen.

## Reclaim Feeder Alarm Screen

LOCAL SELECTOR - Red if the local selector switch for the reclaim feeder is not in the "Remote" position. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the local selector switch is in the "Remote" position.

SAFETY SWITCH - Red if the local safety switch for the reclaim feeder is open. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the safety switch is closed.

ACKNOWLEDGE ALARM button - Pressing this button will cause any flashing indicators on this display to stop flashing. If the alarm condition is no longer on, then it will not be red.

PREV SCREEN button - Pressing this button will display the equipment alarm summary screen.

BACK TO START button - Pressing this button will display the main screen.

## Bucket Elevator Alarm Screen

LOCAL SELECTOR - Red if the local selector switch for conveyor 1 is not in the "Remote" position. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the local selector switch is in the "Remote" position.

SAFETY SWITCH - Red if the local safety switch for conveyor 1 is open. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the safety switch is closed.

PLUG RELAY 1 - Red if the lower plug switch indicates coal piling up in lower part of elevator. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when there is no plug.

PLUG RELAY 2 - Red if the lower plug switch indicates coal piling up in upper part of elevator. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when there is no plug.

ZERO SPEED - Red if the bucket elevator zero speed switch indicates zero speed when the elevator motor is running. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when there is no problem.

ACKNOWLEDGE ALARM button - Pressing this button will cause any flashing indicators on this display to stop flashing. If the alarm condition is no longer on, then it will not be red.

PREV SCREEN button - Pressing this button will display the equipment alarm summary screen.

BACK TO START button - Pressing this button will display the main screen.

## Lowering Well Alarm Screen

LOWERING WELL HIGH - Red if there is a high level at the lowering well. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the lowering well is not at a high level.

ACKNOWLEDGE ALARM button - Pressing this button will cause any flashing indicators on this display to stop flashing. If the alarm condition is no longer on, then it will not be red.

PREV SCREEN button - Pressing this button will display the equipment alarm summary screen.

BACK TO START button - Pressing this button will display the main screen.

## Temperature Alarm Screen

OUTDOOR TEMPERATURE LOW - Red if there is a low temperature, signaling the operator that the conveyors need to be run continuously to avoid freeze-up. It is alternating red/cyan if the alarm has not been acknowledged. It is cyan (light blue) when the temperature is not low. Alarm is currently not functional since the temperature sensor has not been installed.

ACKNOWLEDGE ALARM button - Pressing this button will cause any flashing indicators on this display to stop flashing. If the alarm condition is no longer on, then it will not be red.

PREV SCREEN button - Pressing this button will display the equipment alarm summary screen.

BACK TO START button - Pressing this button will display the main screen.

# Bunker Levels Screen

BUNKER 1 FULL - Red if bunker 1 is full. Otherwise, it is cyan (light blue).

BUNKER 1 HIGH - Red if bunker 1 is high. Otherwise, it is cyan (light blue).

BUNKER 2 FULL - Red if bunker 2 is full. Otherwise, it is cyan (light blue).

BUNKER 2 HIGH - Red if bunker 2 is high. Otherwise, it is cyan (light blue).

BUNKER 3 FULL - Red if bunker 3 is full. Otherwise, it is cyan (light blue).

BUNKER 3 HIGH - Red if bunker 3 is high. Otherwise, it is cyan (light blue).

BUNKER 3 LOW - Red if bunker 3 is low. Otherwise, it is cyan (light blue).

BACK TO START button - Pressing this button will display the main screen.

# Plug/Alignment Screen

ELEV PLUG 1 - Red if coal plugged in lower part of elevator. Otherwise, it is cyan (light blue).

ELEV PLUG 2 - Red if coal plugged in upper part of elevator. Otherwise, it is cyan (light blue).

GATE 1 LWELL - Red if coal plugged in chute between gate 1 and the lowering well. Otherwise, it is cyan (light blue).

GATE 2 - Red if coal plugged in chute above gate 2. Otherwise, it is cyan (light blue).

GATE 2 BKR 1 - Red if coal plugged in chute between gate 2 and bunker 1. Otherwise, it is cyan (light blue).

GATE 3 - Red if coal plugged in chute above gate 3. Otherwise, it is cyan (light blue).

GATE 3 BKR 2 - Red if coal plugged in chute between gate 3 and bunker 2. Otherwise, it is cyan (light blue).

CONV 1 ALIGN - Red if either belt alignment switch for conveyor 1 is open, indicating a problem with the belt. It is cyan (light blue) when both belt alignment switches are closed.

CONV 2 ALIGN - Red if either belt alignment switch for conveyor 2 is open, indicating a problem with the belt. It is cyan (light blue) when both belt alignment switches are closed.

CONV 3 ALIGN - Red if either belt alignment switch for conveyor 3 is open, indicating a problem with the belt. It is cyan (light blue) when both belt alignment switches are closed.

BACK TO START button - Pressing this button will display the main screen.