# Coal Handling PLC Test Plan

Note: All PLC inputs should have been already verified.

1.	Operator Panel E-stop

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Unload

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to conveyor 3

- Start (in this order):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Unloading Feeder

- Push E-stop switch on operator panel

 System E-Stop annunciator sounds (acknowledge to stop flashing and OI panel beep).

 E-Stop Relay 1, E-Stop Relay 2, and System E-Stop messages should be at bottom of  OI panel.

 Conveyor 1 stopped

 Conveyor 2 stopped

 Conveyor 3 stopped

 Bucket elevator stopped

 Unloading feeder stopped

 Ready panel lamp off

- Pull out operator panel E-stop 	 Ready panel lamp on.

 All annunciators and alarms off.

- Change Source feeder to Reclaim

- Change gate 1 to divert to lowering well

- Start (in this order):

Bucket Elevator

Reclaim Feeder

- Push E-stop switch on operator panel

 System E-Stop annunciator sounds (acknowledge to stop flashing and OI panel beep).

 E-Stop Relay 1, E-Stop Relay 2, and System E-Stop messages should be at bottom of  OI panel.

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

- Pull out operator panel E-stop 	 Ready panel lamp on.

 All annunciators and alarms off.

2.	From unloading to lowering well, normal conditions

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Unload

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set gate 1 to divert to lowering well.

- Start bucket elevator 	 bucket elevator panel lamp on

 bucket elevator running.

- Start unloading feeder  unloading feeder panel lamp on

 unloading feeder running.

- Wait a few minutes (optional)

- Stop unloading feeder	 unloading feeder panel lamp off

 unloading feeder stopped.

- Stop bucket elevator 	 bucket elevator panel lamp off

 bucket elevator stopped.

3.	From unloading to lowering well, high level probe

Start with same conditions as start of test 2

- Set gate 1 to divert to lowering well.

- Start bucket elevator

- Start unloading feeder

- Exercise (turn off) lowering well high level probe [simulates high level]

 Lowering well high annunciator sounds (acknowledge to stop flashing and OI panel beep)

 Lowering well high panel lamp on.

 Unloading feeder panel lamp off, unloading feeder stopped.

 Ready panel lamp off

 Purging panel lamp on.

- Wait 2 minutes 	 bucket elevator panel lamp off

 bucket elevator stopped

 Purging panel lamp off.

- Turn on lowering well high level probe 	 Ready panel lamp on.

 Lowering well high panel lamp off

 Lowering well annunciator off

4.	From unloading to lowering well, abnormal conditions

Start with same conditions as start of test 2

- Set gate 1 to divert to lowering well.

- Start bucket elevator

- Start unloading feeder

- Push (Pull?) unloading feeder safety switch

 Unloading feeder annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Safety switch annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Unloading feeder panel lamp off, unloading feeder stopped.

 Bucket elevator panel lamp on, bucket elevator still running.

 Ready panel lamp off

- Restore unloading feeder safety switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start unloading feeder.

- Push (Pull?) bucket elevator safety switch

 Bucket elevator annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Safety switch annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Unloading feeder panel lamp off, unloading feeder stopped.

 Bucket elevator panel lamp off, bucket elevator stopped.

 Ready panel lamp off

- Restore bucket elevator safety switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start bucket elevator

- Start unloading feeder

- Push (Pull?) bucket elevator plug 1 switch

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket Elevator annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket elevator lower plug panel lamp on.

 Unloading feeder panel lamp off, unloading feeder stopped.

 Bucket elevator panel lamp off, bucket elevator stopped.

 Ready panel lamp off

- Restore bucket elevator plug 1 switch 	 Ready panel lamp on.

 Bucket elev low. plug panel lamp off.

 All annunciators and alarms off.

- Start bucket elevator

- Start unloading feeder

- Push bucket elevator plug 2 switch until bucket stops motion (otherwise it will start back up)

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket Elevator annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket elevator upper plug panel lamp on.

 Unloading feeder panel lamp off, unloading feeder stopped.

 Bucket elevator panel lamp off, bucket elevator stopped.

 Ready panel lamp off

- Restore bucket elevator plug 1 switch 	 Ready panel lamp on.

 Bucket elev upp. plug panel lamp off.

 All annunciators and alarms off.

- Start bucket elevator

- Start unloading feeder

- Push (Pull?) gate 1 to lowering well plug switch

 Diverter Gate 1 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Gate 1 plug panel lamp on.

 Unloading feeder panel lamp off, unloading feeder stopped.

 Bucket elevator panel lamp off, bucket elevator stopped.

 Ready panel lamp off

- Restore lowering well plug switch 	 Ready panel lamp on.

 Gate 1 plug panel lamp off.

 All annunciators and alarms off.

5.	From reclaim to lowering well, normal conditions

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set gate 1 to divert to lowering well.

- Start bucket elevator 	 bucket elevator panel lamp on

 bucket elevator running.

- Start reclaim feeder	 reclaim feeder panel lamp on

 reclaim feeder running.

- Wait a few minutes (optional)

- Stop reclaim feeder	 reclaim feeder panel lamp off

 reclaim feeder stopped.

- Wait 2 minutes

- Stop bucket elevator 	 bucket elevator panel lamp off

 bucket elevator stopped.

6.	From reclaim to lowering well, high level probe

Start with same conditions as start of test 5

- Set gate 1 to divert to lowering well.

- Start bucket elevator

- Start reclaim feeder

- Exercise (turn off) lowering well high level probe [simulates high level]

 Lowering well high annunciator sounds (acknowledge to stop flashing and OI panel beep)

 Lowering well high panel lamp on.

 Reclaim feeder panel lamp off, reclaim feeder stopped.

 Ready panel lamp off

 Purging panel lamp on.

- Wait 2 minutes 	 bucket elevator panel lamp off

 bucket elevator stopped

 Purging panel lamp off.

- Turn on lowering well high level probe 	 Ready panel lamp on.

 Lowering well high panel lamp off

 Lowering well annunciator off

7.	From reclaim to lowering well, abnormal conditions

Start with same conditions as start of test 5

- Set gate 1 to divert to lowering well.

- Start bucket elevator

- Start reclaim feeder

- Push (Pull?) reclaim feeder safety switch

 Reclaim feeder annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Safety switch annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Reclaim feeder panel lamp off, reclaim feeder stopped.

 Bucket elevator panel lamp on, bucket elevator still running.

 Ready panel lamp off

- Restore reclaim feeder safety switch 	 Ready panel lamp on.

 Annunciators off

- Start reclaim feeder.

- Push (Pull?) bucket elevator safety switch

 Bucket elevator annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Safety switch annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Reclaim feeder panel lamp off, reclaim feeder stopped.

 Bucket elevator panel lamp off, bucket elevator stopped.

 Ready panel lamp off

- Restore bucket elevator safety switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start bucket elevator

- Start reclaim feeder

- Push (Pull?) bucket elevator plug 1 switch

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket Elevator annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket elevator lower plug panel lamp on.

 Reclaim feeder panel lamp off, reclaim feeder stopped.

 Bucket elevator panel lamp off, bucket elevator stopped.

 Ready panel lamp off

- Restore bucket elevator plug 1 switch 	 Ready panel lamp on.

 Bucket elev low. plug panel lamp off.

 All annunciators and alarms off.

- Start bucket elevator

- Start reclaim feeder

- Push (Pull?) bucket elevator plug 2 switch

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket Elevator annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket elevator upper plug panel lamp on.

 Reclaim feeder panel lamp off, reclaim feeder stopped.

 Bucket elevator panel lamp off, bucket elevator stopped.

 Ready panel lamp off

- Restore bucket elevator plug 1 switch 	 Ready panel lamp on.

 Bucket elev upp. plug panel lamp off.

 All annunciators and alarms off.

- Start bucket elevator

- Start reclaim feeder

- Push (Pull?) gate 1 to lowering well plug switch

 Diverter Gate 1 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Gate 1 plug panel lamp on.

 Reclaim feeder panel lamp off, reclaim feeder stopped.

 Bucket elevator panel lamp off, bucket elevator stopped.

 Ready panel lamp off

- Restore lowering well plug switch 	 Ready panel lamp on.

 Gate 1 plug panel lamp off.

 All annunciators and alarms off.

8.	Reclaim and unloading feeders lockouts

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set gate 1 to divert to lowering well.

- Start reclaim feeder	 will not start

- Start unloading feeder	 will not start

- Start bucket elevator 	 bucket elevator panel lamp on

 bucket elevator running.

- Start unloading feeder	 will not start

- Stop bucket elevator 	 bucket elevator panel lamp off

 bucket elevator stopped.

- Change source feeder switch to Unload.

- Start unloading feeder	 will not start

- Start reclaim feeder	 will not start

- Start bucket elevator 	 bucket elevator panel lamp on

 bucket elevator running.

- Start reclaim feeder	 will not start

- Stop bucket elevator 	 bucket elevator panel lamp off

 bucket elevator stopped.

9.	Gate 1 safety switch

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set gate 1 to divert to conveyor 1.

- Push (Pull?) gate 1 safety switch

 Safety Switch annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 1 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Ready panel lamp off

- Set gate 1 to divert to lowering well  gate 1 does not move.

- Restore gate 1 safety switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Set gate 1 to divert to lowering well  gate 1 moves to lowering well position.

- Set gate 1 to divert to conveyor 1  gate 1 moves to conveyor position.

10.	Gate 2 safety switch

Start with same conditions as start of test 9 (gate 1 safety switch).

- Set gate 1 to divert to conveyor 1.

- Set gate 2 to divert to conveyor 2.

- Push (Pull?) gate 2 safety switch

 Safety Switch annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 2 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Ready panel lamp off

- Set gate 2 to divert to bunker 1  gate 2 does not move.

- Restore gate 2 safety switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Set gate 2 to divert to bunker 1  gate 2 moves to bunker 1 position.

- Set gate 2 to divert to conveyor 2  gate 2 moves to conveyor 2 position.

11.	Gate 3 safety switch

Start with same conditions as start of test 9 (gate 1 safety switch).

- Set gate 1 to divert to conveyor 1.

- Set gate 2 to divert to conveyor 2.

- Set gate 3 to divert to conveyor 3.

- Push (Pull?) gate 3 safety switch

 Safety Switch annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 3 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Ready panel lamp off

- Set gate 3 to divert to Bunker 2  gate 2 does not move.

- Restore gate 3 safety switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Set gate 3 to divert to bunker 2  gate 3 moves to bunker 2 position.

- Set gate 3 to divert to conveyor 3  gate 3 moves to conveyor 3 position.

12.	Conveyor 1 abnormal conditions

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to conveyor 3

- Start (in this order):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Pull Conveyor 1 E-stop pull cord

 Pull Cord E-Stop annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 1 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

 Conveyor 2 running

 Conveyor 3 running

- Restore Conveyor 1 E-stop switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) Conveyor 1 safety switch

 Safety Switch annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 1 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

 Conveyor 2 running

 Conveyor 3 running

- Restore Conveyor 1 safety switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) one of the Conveyor 1 belt alignment switches

 Belt Alignment annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 1 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

 Conveyor 2 running

 Conveyor 3 running

- Restore Conveyor 1 belt alignment switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 1

Bucket Elevator

Reclaim Feeder

- (Optional) Repeat steps h – j for the other belt alignment switch.

13.	Conveyor 2 abnormal conditions

Start with same conditions as test 12 (conveyor 1 abnormal conditions):

- Start (if not already started):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Pull Conveyor 2 E-stop pull cord

 Pull Cord E-Stop annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 2 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

 Conveyor 3 running

- Restore Conveyor 2 E-stop switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) Conveyor 2 safety switch

 Safety Switch annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 2 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

 Conveyor 3 running

- Restore Conveyor 2 safety switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Pull one of the Conveyor 2 belt alignment switches

 Belt Alignment annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 2 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

 Conveyor 3 running

- Restore Conveyor 2 belt alignment switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- (Optional) Repeat steps h – j for the other belt alignment switch.

14.	Conveyor 3 abnormal conditions

Start with same conditions as test 12 (conveyor 1 abnormal conditions):

- Start (if not already started):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Pull Conveyor 3 E-stop pull cord

 Pull Cord E-Stop annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 3 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 3 stopped

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

- Restore Conveyor 3 E-stop switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) Conveyor 3 safety switch

 Safety Switch annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 3 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 3 stopped

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

- Restore Conveyor 3 safety switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Pull one of the Conveyor 3 belt alignment switches

 Belt Alignment annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 3 annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 3 stopped

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

- Restore Conveyor 3 belt alignment switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- (Optional) Repeat steps h – j for the other belt alignment switch.

15.	Conveyor 1 abnormal conditions with Unloading feeder

Repeat test 12, but with Source Feeder set to Unload

Substitute “Unloading Feeder” for “Reclaim Feeder” in steps.

16.	Conveyor 2 abnormal conditions with Unloading feeder

Repeat test 13, but with Source Feeder set to Unload

Substitute “Unloading Feeder” for “Reclaim Feeder” in steps.

17.	Conveyor 3 abnormal conditions with Unloading feeder

Repeat test 14, but with Source Feeder set to Unload

Substitute “Unloading Feeder” for “Reclaim Feeder” in steps.

18.	Gate plugs with path from unloading to bunker 3

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Unload

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to conveyor 3

- Start (in this order):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Unloading Feeder

- Push (Pull?) gate 1 to lowering well plug switch

 Gate 1 to lowering well alarm message on OI Panel.

 Gate 1 to lowering well plug lamp on.

 No equipment should be stopped.

- Restore lowering well plug switch.

- Push Bucket Elevator Plug 2 switch (above end of bucket)

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket Elevator alarm flashes (acknowledge to stop flashing).

 Bucket Elevator plug 2 lamp on.

 Bucket elevator stopped

 Unloading feeder stopped

 Ready panel lamp off

 Conveyor 1 running

 Conveyor 2 running

 Conveyor 3 running

- Restore Bucket Elevator Plug 2 switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Bucket Elevator

Unloading Feeder

- Push gate 2 to bunker 1 plug switch

 Gate 2 to bunker 1 alarm message on OI Panel.

 Gate 2 to bunker 1 plug lamp on.

 No equipment should be stopped.

- Restore gate 2 to bunker 1 plug switch.

- Push Gate 2 Plug switch (at end of conveyor 1)

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 2 alarm flashes (acknowledge to stop flashing).

 Gate 2 plugged lamp on.

 Conveyor 1 stopped

 Bucket elevator stopped

 Unloading feeder stopped

 Ready panel lamp off

 Conveyor 2 running

 Conveyor 3 running

- Restore Gate 2 Plug switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 2

Conveyor 1

Bucket Elevator

Unloading Feeder

- Push (Pull?) gate 3 to bunker 2 plug switch

 Gate 3 to bunker 2 alarm message on OI Panel.

 Gate 3 to bunker 2 plug lamp on.

 No equipment should be stopped.

- Restore gate 3 to bunker 2 plug switch.

- Push (Pull?) Gate 3 Plug switch (above gate 3?)

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 3 alarm flashes (acknowledge to stop flashing).

 Gate 3 plugged lamp on.

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Unloading feeder stopped

 Ready panel lamp off

 Conveyor 3 running

- Restore Gate 3 Plug switch 	 Ready panel lamp on.

 All annunciators and alarms off.

19.	Gate plugs with path from reclaim to bunker 3

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to conveyor 3

- Start (in this order):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) gate 1 to lowering well plug switch

 Gate 1 to lowering well alarm message on OI Panel.

 Gate 1 to lowering well plug lamp on.

 No equipment should be stopped.

- Restore lowering well plug switch.

- Push (Pull?) Bucket Elevator Plug 2 switch (above gate 1?)

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket Elevator alarm flashes (acknowledge to stop flashing).

 Bucket Elevator plug 2 lamp on.

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

 Conveyor 1 running

 Conveyor 2 running

 Conveyor 3 running

- Restore Bucket Elevator Plug 2 switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Bucket Elevator

Reclaim Feeder

- Push (Pull?) gate 2 to bunker 1 plug switch

 Gate 2 to bunker 1 alarm message on OI Panel.

 Gate 2 to bunker 1 plug lamp on.

 No equipment should be stopped.

- Restore gate 2 to bunker 1 plug switch.

- Push (Pull?) Gate 2 Plug switch (above gate 2?)

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 2 alarm flashes (acknowledge to stop flashing).

 Gate 2 plugged lamp on.

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

 Conveyor 2 running

 Conveyor 3 running

- Restore Gate 2 Plug switch 	 Ready panel lamp on.

 All annunciators and alarms off.

- Start (in this order):

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) gate 3 to bunker 2 plug switch

 Gate 3 to bunker 2 alarm message on OI Panel.

 Gate 3 to bunker 2 plug lamp on.

 No equipment should be stopped.

- Restore gate 3 to bunker 2 plug switch.

- Push (Pull?) Gate 3 Plug switch (above gate 3?)

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 3 alarm flashes (acknowledge to stop flashing).

 Gate 3 plugged lamp on.

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

 Conveyor 3 running

- Restore Gate 3 Plug switch 	 Ready panel lamp on.

 All annunciators and alarms off.

20.	Gate plugs with path from unloading to bunker 2

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Unload

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to bunker 2

- Start (in this order):

Conveyor 2

Conveyor 1

Bucket Elevator

Unloading Feeder

- Push (Pull?) gate 3 to bunker 2 plug switch

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 3 alarm flashes (acknowledge to stop flashing).

 Gate 3 to bunker 2 plug lamp on.

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Unloading feeder stopped

 Ready panel lamp off

- Restore Gate 3 to Bunker 2 Plug switch 	 Ready panel lamp on.

 All annunciators and alarms off.

21.	Gate plugs with path from unloading to bunker 2

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to bunker 2

- Start (in this order):

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) gate 3 to bunker 2 plug switch

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 3 alarm flashes (acknowledge to stop flashing).

 Gate 3 to bunker 2 plug lamp on.

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

- Restore Gate 3 to Bunker 2 Plug switch 	 Ready panel lamp on.

 All annunciators and alarms off.

22.	Gate plugs with path from unloading to Bunker 1

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Unload

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to bunker 1

Gate 3 diverted to bunker 2

- Start (in this order):

Conveyor 1

Bucket Elevator

Unloading Feeder

- Push gate 2 to bunker 1 plug switch for 3 seconds

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 2 alarm flashes (acknowledge to stop flashing).

 Gate 2 to bunker 1 plug lamp on.

 Conveyor 1 stopped

 Bucket elevator stopped

 Unloading feeder stopped

 Ready panel lamp off

- Restore Gate 2 to Bunker 1 Plug switch 	 Ready panel lamp on.

 All annunciators and alarms off.

23.	Gate plugs with path from reclaim to Bunker 1

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to bunker 1

Gate 3 diverted to bunker 2

- Start (in this order):

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) gate 2 to bunker 1 plug switch

 Chute Plugged annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 2 alarm flashes (acknowledge to stop flashing).

 Gate 2 to bunker 1 plug lamp on.

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

- Restore Gate 2 to Bunker 1 Plug switch 	 Ready panel lamp on.

 All annunciators and alarms off.

24.	Bunker 3 High Level

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to conveyor 3

- Start (in this order):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) bunker 3 high switch

 Bunker 3 Full annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bunker 3 Full Level lamp on.

 Conveyor 3 stopped

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

- Restore bunker 3 high switch 	 Ready panel lamp on.

 Bunker 3 High Level lamp off. 		 All annunciators and alarms off.

25.	Bunker 3 Low Level

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Push (Pull?) bunker 3 low switch

 Bunker 3 Low annunciator sounds (acknowledge to stop flashing and OI panel beep).

- Restore Bunker 3 low switch 	 All annunciators and alarms off.

26.	Bunker 3 Full Level [Cannot test until probe installed]

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to conveyor 3

- Start (in this order):

Conveyor 3

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) bunker 3 full switch

 Bunker 3 Full alarm message on OI panel.

 Bunker 3 full lamp on.

 Purging lamp on.

 Conveyor 3 running

 Conveyor 2 running

 Conveyor 1 running

 Bucket elevator running

 Reclaim feeder stopped

 Ready panel lamp off

- Wait 2 minutes

 Purging lamp off.

 Conveyor 3 stopped

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Ready panel lamp on

27.	Bunker 2 High Level [Cannot test until probe installed]

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to bunker 2

- Start (in this order):

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) bunker 2 high switch

 System E-Stop annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bunker 2 High Level lamp on.

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

- Restore Bunker 2 high switch 	 Ready panel lamp on.

 Bunker 2 High Level lamp off. 			 All annunciators and alarms off.

28.	Bunker 2 Full Level [Cannot test until probe installed]

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to bunker 2

- Start (in this order):

Conveyor 2

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) bunker 2 full switch

 Bunker 2 Full alarm message on OI panel.

 Bunker 2 full lamp on.

 Purging lamp on.

 Conveyor 2 running

 Conveyor 1 running

 Bucket elevator running

 Reclaim feeder stopped

 Ready panel lamp off

- Wait 2 minutes

 Purging lamp off.

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Ready panel lamp on

- Restore Bunker 2 full switch 	 Ready panel lamp on.

 Bunker 2 Full Level lamp off. 			 All annunciators and alarms off.

29.	Bunker 1 High Level [Cannot test until probe installed]

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to bunker 1

- Start (in this order):

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) bunker 2 high switch

 System E-Stop annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bunker 1 High Level lamp on.

 Conveyor 1 stopped

 Bucket elevator stopped

 Reclaim feeder stopped

 Ready panel lamp off

- Restore Bunker 1 high switch 	 Ready panel lamp on.

 Bunker 1 High Level lamp off. 			 All annunciators and alarms off.

30.	Bunker 1 Full Level [Cannot test until probe installed]

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to bunker 1

- Start (in this order):

Conveyor 1

Bucket Elevator

Reclaim Feeder

- Push (Pull?) bunker 1 full switch

 Bunker 1 Full alarm message on OI panel.

 Bunker 1 full lamp on.

 Purging lamp on.

 Conveyor 1 running

 Bucket elevator running

 Reclaim feeder stopped

 Ready panel lamp off

- Wait 2 minutes

 Purging lamp off.

 Conveyor 1 stopped

 Bucket elevator stopped

 Ready panel lamp on

- Restore Bunker 1 full switch 	 Ready panel lamp on.

 Bunker 1 Full Level lamp off. 			 All annunciators and alarms off.

31.	Auto Mode from reclaim to Bunker 3

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set up path:

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to conveyor 3

- Set Operation Mode to Auto

- Hold System Auto Control to Start/Restart for 15 seconds

 Warning Horns should sound.

 Conveyor 3 starts

 Conveyor 2 starts

 Conveyor 1 starts

 Bucket elevator starts

 Reclaim feeder starts

 Warning Horns should silence.

- Wait a few minutes (optional)

- Hold System Auto Control to Purge/Stop for at least two seconds

 Purging lamp on.

 Conveyor 3 running

 Conveyor 2 running

 Conveyor 1 running

 Bucket elevator running

 Reclaim feeder stopped

 Ready panel lamp on

- Wait 2 minutes

 Purging lamp off.

 Conveyor 3 stopped

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Ready panel lamp on

32.	Auto Mode from unload to Bunker 3

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Unload

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set up path:

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to conveyor 3

- Set Operation Mode to Auto

- Hold System Auto Control to Start/Restart for 15 seconds

 Warning Horns should sound.

 Conveyor 3 starts

 Conveyor 2 starts

 Conveyor 1 starts

 Bucket elevator starts

 Unloading feeder starts

 Warning Horns should silence.

- Wait a few minutes (optional)

- Hold System Auto Control to Purge/Stop for at least two seconds

 Purging lamp on.

 Conveyor 3 running

 Conveyor 2 running

 Conveyor 1 running

 Bucket elevator running

 Unloading feeder stopped

 Ready panel lamp on

- Wait 2 minutes

 Purging lamp off.

 Conveyor 3 stopped

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Ready panel lamp on

33.	Auto Mode from reclaim to Bunker 2

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set up path:

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to bunker 2

- Set Operation Mode to Auto

- Hold System Auto Control to Start/Restart for 15 seconds

 Warning Horns should sound.

 Conveyor 2 starts

 Conveyor 1 starts

 Bucket elevator starts

 Reclaim feeder starts

 Warning Horns should silence.

- Wait a few minutes (optional)

- Hold System Auto Control to Purge/Stop for at least two seconds

 Purging lamp on.

 Conveyor 2 running

 Conveyor 1 running

 Bucket elevator running

 Reclaim feeder stopped

 Ready panel lamp on

- Wait 2 minutes

 Purging lamp off.

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Ready panel lamp on

34.	Auto Mode from unload to Bunker 2

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Unload

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set up path:

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to bunker 2

- Set Operation Mode to Auto

- Hold System Auto Control to Start/Restart for 15 seconds

 Warning Horns should sound.

 Conveyor 2 starts

 Conveyor 1 starts

 Bucket elevator starts

 Unloading feeder starts

 Warning Horns should silence.

- Wait a few minutes (optional)

- Hold System Auto Control to Purge/Stop for at least two seconds

 Purging lamp on.

 Conveyor 2 running

 Conveyor 1 running

 Bucket elevator running

 Unloading feeder stopped

 Ready panel lamp on

- Wait 2 minutes

 Purging lamp off.

 Conveyor 2 stopped

 Conveyor 1 stopped

 Bucket elevator stopped

 Ready panel lamp on

35.	Auto Mode from reclaim to Bunker 1

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set up path:

Gate 1 diverted to conveyor 1

Gate 2 diverted to bunker 1

- Set Operation Mode to Auto

- Hold System Auto Control to Start/Restart for 15 seconds

 Warning Horns should sound.

 Conveyor 1 starts

 Bucket elevator starts

 Reclaim feeder starts

 Warning Horns should silence.

- Wait a few minutes (optional)

- Hold System Auto Control to Purge/Stop for at least two seconds

 Purging lamp on.

 Conveyor 1 running

 Bucket elevator running

 Reclaim feeder stopped

 Ready panel lamp on

- Wait 2 minutes

 Purging lamp off.

 Conveyor 1 stopped

 Bucket elevator stopped

 Ready panel lamp on

36.	Auto Mode from unload to Bunker 1

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Unload

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set up path:

Gate 1 diverted to conveyor 1

Gate 2 diverted to bunker 1

- Set Operation Mode to Auto

- Hold System Auto Control to Start/Restart for 15 seconds

 Warning Horns should sound.

 Conveyor 1 starts

 Bucket elevator starts

 Unloading feeder starts

 Warning Horns should silence.

- Wait a few minutes (optional)

- Hold System Auto Control to Purge/Stop for at least two seconds

 Purging lamp on.

 Conveyor 1 running

 Bucket elevator running

 Unloading feeder stopped

 Ready panel lamp on

- Wait 2 minutes

 Purging lamp off.

 Conveyor 1 stopped

 Bucket elevator stopped

 Ready panel lamp on

37.	Auto Mode from reclaim to Lowering Well

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Reclaim

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set up path:

Gate 1 diverted to lowering well

- Set Operation Mode to Auto

- Hold System Auto Control to Start/Restart for 15 seconds

 Warning Horns should sound.

 Bucket elevator starts

 Reclaim feeder starts

 Warning Horns should silence.

- Wait a few minutes (optional)

- Hold System Auto Control to Purge/Stop for at least two seconds

 Purging lamp on.

 Bucket elevator running

 Reclaim feeder stopped

 Ready panel lamp on

- Wait 2 minutes

 Purging lamp off.

 Bucket elevator stopped

 Ready panel lamp on

38.	Auto Mode from unload to Lowering Well

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Unload

Operation Mode – Manual

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

- Set up path:

Gate 1 diverted to lowering well

- Set Operation Mode to Auto

- Hold System Auto Control to Start/Restart for 15 seconds

 Warning Horns should sound.

 Bucket elevator starts

 Unloading feeder starts

 Warning Horns should silence.

- Wait a few minutes (optional)

- Hold System Auto Control to Purge/Stop for at least two seconds

 Purging lamp on.

 Bucket elevator running

 Unloading feeder stopped

 Ready panel lamp on

- Wait 2 minutes

 Purging lamp off.

 Bucket elevator stopped

 Ready panel lamp on

39.	Feeder and Elevator Remote Jog stations

Start with:

All equipment jog stations in Rem position

Warning Horns – Off

Source Feeder – Unload

Operation Mode – Off

System Auto Control – Center (off)

Emergency Stop – Pulled Out

All annunciator indications are off.

Ready lamp should be on.

Gate 1 diverted to conveyor 1

Gate 2 diverted to conveyor 2

Gate 3 diverted to bunker 2

- Switch Unloading Feeder Jog/Remote switch to Off position:

 Local Selector annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Unload Feeder alarm flashes (acknowledge to stop flashing).

- Switch Unloading Feeder Jog/Remote switch to Jog position

 Unloading feeder should start.

- Switch Unloading Feeder Jog/Remote switch to Rem position

 Unloading feeder should stop.

 All annunciators and alarms off.

- Switch Bucket Elevator Jog/Remote switch to Off position:

 Local Selector annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Bucket Elevator alarm flashes (acknowledge to stop flashing).

- Switch Bucket Elevator Jog/Remote switch to Jog position

 Bucket Elevator should start.

- Switch Bucket Elevator Jog/Remote switch to Rem position

 Bucket Elevator should stop.

 All annunciators and alarms off.

- Switch Reclaim Feeder Jog/Remote switch to Off position:

 Reclaim Feeder alarm flashes (acknowledge to stop flashing).

- Switch Reclaim Feeder Jog/Remote switch to Rem position

 All annunciators and alarms off.

- Switch Source Feeder to Reclaim position.

- Switch Reclaim Feeder Jog/Remote switch to Off position:

 Local Selector annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Reclaim Feeder alarm flashes (acknowledge to stop flashing).

- Switch Unloading Feeder Jog/Remote switch to Jog position

 Reclaim feeder should start.

- Switch Reclaim Feeder Jog/Remote switch to Rem position

 Reclaim feeder should stop.

 All annunciators and alarms off.

40.	Gate 1 and Conveyor 1 Remote Jog stations

Start with:

Same conditions as for test 39 (Feeder and Elevator Remote Jog stations)

- Switch Gate 1 Jog/Remote switch to Off position:

 Local Selector annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 1 alarm flashes (acknowledge to stop flashing).

- Press Lowering Well push button

 Nothing should happen.

- Press Conveyor 1 push button

 Nothing should happen.

- Switch Gate 1 Jog/Remote switch to Jog position

- Press Lowering Well push button

 Gate should swing to lowering well position.

- Press Conveyor 1 push button

 Gate should swing to conveyor 1 position.

- Switch Gate 1 Jog/Remote switch to Rem position

 All annunciators and alarms off.

- Switch Conveyor 1 Jog/Remote switch to Off position:

 Local Selector annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 1 alarm flashes (acknowledge to stop flashing).

- Switch Conveyor 1 Jog/Remote switch to Jog position

 Conveyor 1 should start.

- Switch Conveyor 1 Jog/Remote switch to Off then Rem position

 Conveyor 1 should stop.

 All annunciators and alarms off.

41.	Gate 2 and Conveyor 2 Remote Jog stations

Start with:

Same conditions as for test 39 (Feeder and Elevator Remote Jog stations)

- Switch Gate 2 Jog/Remote switch to Off position:

 Local Selector annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 2 alarm flashes (acknowledge to stop flashing).

- Press Bunker 1 push button

 Nothing should happen.

- Press Conveyor 2 push button

 Nothing should happen.

- Switch Gate 2 Jog/Remote switch to Jog position

- Press Bunker 1 push button

 Gate should swing to bunker 1 position.

- Press Conveyor 2 push button

 Gate should swing to conveyor 2 position.

- Switch Gate 2 Jog/Remote switch to Rem position

 All annunciators and alarms off.

- Switch Conveyor 2 Jog/Remote switch to Off position:

 Local Selector annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 2 alarm flashes (acknowledge to stop flashing).

- Switch Conveyor 2 Jog/Remote switch to Jog position

 Conveyor 2 should start.

- Switch Conveyor 2 Jog/Remote switch to Off then Rem position

 Conveyor 2 should stop.

 All annunciators and alarms off.

42.	Gate 3 and Conveyor 3 Remote Jog stations

Start with:

Same conditions as for test 39 (Feeder and Elevator Remote Jog stations)

- Switch Gate 3 Jog/Remote switch to Off position:

 Local Selector annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Diverter Gate 3 alarm flashes (acknowledge to stop flashing).

- Press Bunker 2 push button

 Nothing should happen.

- Press Conveyor 3 push button

 Nothing should happen.

- Switch Gate 3 Jog/Remote switch to Jog position

- Press Bunker 2 push button

 Gate should swing to bunker 2 position.

- Press Conveyor 3 push button

 Gate should swing to conveyor 3 position.

- Switch Gate 3 Jog/Remote switch to Rem position

 All annunciators and alarms off.

- Switch Conveyor 3 Jog/Remote switch to Off position:

 Local Selector annunciator sounds (acknowledge to stop flashing and OI panel beep).

 Conveyor 3 alarm flashes (acknowledge to stop flashing).

- Switch Conveyor 3 Jog/Remote switch to Jog position

 Conveyor 3 should start.

- Switch Conveyor 3 Jog/Remote switch to Off then Rem position

 Conveyor 3 should stop.

 All annunciators and alarms off.