Communications Test Plan

Numbers refer to Full Test Plan

Monday Lab (TWet_Unl, RWet_Unl, Blend, React_1, Ion_Exc_1, CIP_1

Will need the following units operational from the Tuesday lab: Ion_Exc_2

A. Test of RWet_Unl and TWet_Unl with Blend

Start with:

TWet_Unl Shutdown

RWet_Unl Shutdown

Set LI2110 to 0 (from Blend)

Set LI2130 to 0 (from Blend)

From TWet_Unl,

Initiate transfer to T-2110

Set FT1148 to 200

From RWet_Unl

Initiate transfer to T-2110 – should not actually happen

Set LI2110 to 96 (from Blend)

Wait for TWet_Unl to shut down

From RWet_Unl

Initiate transfer to T-2130

Set FT1198 to 200

From TWet_Unl,

Initiate transfer to T-2130 – should not actually happen

Set LI2130 to 96 (from Blend)

Wait for RWet_Unl to shut down

B. Test of CIP_1 with Soda_Ash (should have been done last week)

Start with:

Soda_Ash Shutdown

CIP_1 Shutdown

Run Test 6e

C. Test of React_1 with Blend, QA_Smpl, Ion_Exc_1, Ion_Exc_2

Start with:

React_1 Shutdown

Blend shutdown

QA_Smpl Shutdown

Ion_Exc_1 Shutdown

Ion_Exc_2 Shutdown

Run Test 9b, except both Ion_Exc shutdown

D. Test of React_1 with CIP_1

Start with:

React_1 Shutdown

Blend shutdown

CIP_1 Online/Recycle

Run Test 13e

E. Test of Ion_Exc_1 with CIP_1

Start with:

Ion_Exc_1 Shutdown

CIP_1 Online/Recycle

Run Test 13c

F. Test of CIP_1 abnormal conditions involving communications

1.	Start with:

React_1 Shutdown

Run Test 13e until CIP_1 has path set

Operator initiates React_1 Shutdown

CIP_1 should shutdown automatically

2.	Start with:

Ion_Exc_1 Online/Recycle

Run Test 13c until CIP_1 has path set

Operator initiates Ion_Exc_1 Shutdown

CIP_1 should shutdown automatically

Tuesday lab (TDry_Unl, RDry_Unl, Dry_Store, React_2, Ion_Exc_2, Stor_Tnk_LO_1)

Will need the following units operational from the Monday lab: Blend, QASmpl, Ion_Exc_1, CIP_1

G. Test of RDry_Unl and TDry_Unl with Dry_Store

Start with:

TDry_Unl Shutdown

RDry_Unl Shutdown

Set LI2210 to 0 (from Dry_Store)

Set LI2230 to 0 (from Dry_Store)

From TDry_Unl,

Initiate transfer to T-2210

From RDry_Unl

Initiate transfer to T-2210 – should not actually happen

Set LI2210 to 96 (from Dry_Store)

Wait for TDry_Unl to shut down

From RDry_Unl

Initiate transfer to T-2230

From TDry_Unl,

Initiate transfer to T-2230 – should not actually happen

Set LI2230 to 96 (from Dry_Store)

Wait for RDry_Unl to shut down

Set LI2210 to 0 (from Dry_Store)

Set LI2220 to 0 (from Dry_Store)

From RDry_Unl,

Initiate transfer to T-2220

Wait for Dry_StoIn path to be running

From Dry_StoIn

Initiate E-Shutdown

RDry_Unl should E-shutdown

From RDry_Unl,

Initiate transfer to T-2220

Wait for Dry_StoIn path to be running

Initiate E-Shutdown

Dry_StoIn should E-shutdown

Set LI2210 to 0 (from Dry_Store)

Set LI2220 to 0 (from Dry_Store)

From TDry_Unl,

Initiate transfer to T-2220

Wait for Dry_StoIn path to be running

From Dry_StoIn

Initiate E-Shutdown

TDry_Unl should E-shutdown

From TDry_Unl,

Initiate transfer to T-2220

Wait for Dry_StoIn path to be running

Initiate E-Shutdown

Dry_StoIn should E-shutdown

H. Test of React_2 with Dry_StoOt, Blend, QA_Smpl, Ion_Exc_1, Ion_Exc_2

Start with:

React_2 Shutdown

Dry_StoOt Shutdown

Blend shutdown

QA_Smpl Shutdown

Ion_Exc_1 Shutdown

Ion_Exc_2 Shutdown

Run Test 18b, except both Ion_Exc shutdown

I. Test of React_2 with CIP_1

Start with:

React_2 Shutdown

Blend shutdown

CIP_1 Online/Recycle

Run Test 13f

J. Test of Ion_Exc_2 with CIP_1

Start with:

Ion_Exc_2 Shutdown

CIP_1 Online/Recycle

Run Test 13d

K. Test of Ion_Exc_2 with Stor_Tnk_1

Start with:

Ion_Exc_2 Shutdown

LI5000 to 40 (from Stor_Tnk_1)

Run Test 19b until Online is initiated

Set LI5100 to 96 (from Stor_Tnk_1)

Ion_Exc_2 should EShutdown

L. Test of Stor_Tnk_1 with CIP_1

Start with:

Stor_Tnk_1 Shutdown

CIP_1 Online/Recycle

Run Test 13b

M. Test of units using CIP_1 abnormal conditions (React_2, Ion_Exc_2, Stor_Tnk_1) involving communications

1.	Start with:

React_2 Shutdown

CIP_1 Online/recycle

Run Test 13f until CIP_1 has path set

Operator initiates CIP_1 Shutdown

React_2 should shutdown automatically

2.	Start with:

Ion_Exc_2 Shutdown

CIP_1 Online/recycle

Run Test 13d until CIP_1 has path set

Operator initiates CIP_1 Shutdown

Ion_Exc_2  should shutdown automatically

3.	Start with:

Stor_Tnk_1 Shutdown

CIP_1 Online/recycle

Run Test 13b until CIP_1 has path set

Operator initiates CIP_1 Shutdown

Stor_Tnk_1 should shutdown automatically

Wed. Distance Students (Dry_Add)

Will need the following units operational from the other labs: Blend, Wet_Add (stub)

N. Test of Dry_Add with Blend

Check that T2150 and T2160 levels can be read from Blend:

Change levels in Blend

O. Test of Dry_Add with Wet_Add

Start with:

Dry_Add Shutdown

Set LI2150 to 0 (from Blend)

Set LI2160 to 0 (from Blend)

At Wet_Add stub

Set Wet_Add_Export_Info to 1

From Dry_Add

Initiate Makeup with destination T-2150 – should not actually happen

At Wet_Add stub

Set Wet_Add_Export_Info to 2

From Dry_Add

Initiate Makeup with destination T-2150 – should progress normall

Wednesday lab (RPow_Unl, TPow_Unl, React_3, Ion_Exc_3, Ion_Exc_4, Stor_Tnk_2)

Will need the following units operational from other labs: none

P. Test of RPow_Unl with React_3

Start with:

TPow_Unl Shutdown

RPow_Unl Shutdown

Set LI2610 to 0 (from React_3)

Set LI2630 to 0 (from React_3)

From TPow_Unl,

Initiate transfer to T-2610

From RPow_Unl

Initiate transfer to T-2610 – should not actually happen

Set LI2610 to 96 (from React_3)

Wait for TPow_Unl to shut down

From RPow_Unl

Initiate transfer to T-2630

Set LI2630 to 96 (from React_3)

Wait for RPow_Unl to shut down

Q. Test of TPow_Unl with React_3

Start with:

TPow_Unl Shutdown

RPow_Unl Shutdown

Set LI2610 to 0 (from React_3)

Set LI2630 to 0 (from React_3)

From RPow_Unl,

Initiate transfer to T-2610

From TPow_Unl

Initiate transfer to T-2610 – should not actually happen

Set LI2610 to 96 (from React_3)

Wait for RPow_Unl to shut down

From TPow_Unl

Initiate transfer to T-2630

Set LI2630 to 96 (from React_3)

Wait for RPow_Unl to shut down

R. Test of React_3 with Ion_Exc_3

Start with:

React_3 Shutdown

Ion_Exc_3 Online

Run Test 22b

S. Test of React_3 with Ion_Exc_3 and Ion_Exc_4

Start with:

React_3 Shutdown

Ion_Exc_3 Shutdown

Ion_Exc_4 Shutdown

Operator initiate React_3_Flush

Ion_Exc_3 should be commanded to startup and React_3 Flush should progress when it is online

Eventually, React_3 goes to Shutdown (by auto-start)

T. Test of Ion_Exc_3 with Stor_Tnk_2

Start with:

Ion_Exc_3 Shutdown

LI5200 to 40 (from Stor_Tnk_LO_2)

Run Test 23b until Online is initiated

Set LI5200 to 96 (from Stor_Tnk_LO_2)

Ion_Exc_3 should EShutdown

U. Test of Ion_Exc_4 with Stor_Tnk_2

Start with:

Ion_Exc_4 Shutdown

LI5200 to 40 (from Stor_Tnk_LO_2)

Run Test 24b until Online is initiated

Set LI5200 to 96 (from Stor_Tnk_LO_2)

Ion_Exc_4 should EShutdown

Wed/Thurs Distance lab (React_4, Ion_Exc_5, Ion_Exc_6, Stor_Tnk_LO_3, CIP_2)

Will need the following units operational from other labs: none

V. Test of React_4 with Ion_Exc_5 and Ion_Exc_6

Start with:

React_4 Shutdown

Ion_Exc_5 Shutdown

Ion_Exc_6 Shutdown

Run Test 22b

Ion_Exc_5 should be commanded to startup and React_4 MakeBatch should progress when it is online

Eventually, React_4 goes to Shutdown (by auto-start)

W. Test of React_4 with CIP_2

Start with:

React_4 Shutdown

CIP_2 Online/Recycle

Run Test 33d

X. Test of Ion_Exc_5 with CIP_2

Start with:

Ion_Exc_5 Shutdown

CIP_2 Online/Recycle

Run Test 33b

Y. Test of Ion_Exc_6 with CIP_2

Start with:

Ion_Exc_6 Shutdown

CIP_2 Online/Recycle

Run Test 33c

Z. Test of Ion_Exc_5 with Stor_Tnk_3

Start with:

Ion_Exc_5 Shutdown

LI5300 to 40 (from Stor_Tnk_LO_3)

Run Test 28b until Online is initiated

Set LI5300 to 96 (from Stor_Tnk_LO_3)

Ion_Exc_5 should EShutdown

AA. Test of Ion_Exc_6 with Stor_Tnk_3

Start with:

Ion_Exc_4 Shutdown

LI5300 to 40 (from Stor_Tnk_LO_3)

Run Test 29b until Online is initiated

Set LI5300 to 96 (from Stor_Tnk_LO_3)

Ion_Exc_6 should EShutdown

AB. Test of units using CIP_2 abnormal conditions (React_4, Ion_Exc_5, Ion_Exc_6) involving communications

1.	Start with:

React_4 Shutdown

CIP_2 Online/recycle

Run Test xx until CIP_2 has path set

Operator initiates CIP_2 Shutdown

React_4 should shutdown automatically

2.	Start with:

Ion_Exc_5 Shutdown

CIP_2 Online/recycle

Run Test 33b until CIP_2 has path set

Operator initiates CIP_2 Shutdown

Ion_Exc_5  should shutdown automatically

3.	Start with:

Ion_Exc_6 Shutdown

CIP_2 Online/recycle

Run Test 33c until CIP_2 has path set

Operator initiates CIP_2 Shutdown

Ion_Exc_6  should shutdown automatically

AB. Test of CIP_2 abnormal conditions involving communications

1.	Start with:

React_4 Shutdown

Run Test xx until CIP_2 has path set

Operator initiates React_4 Shutdown

CIP_2 should shutdown automatically

2.	Start with:

Ion_Exc_5 Online/Recycle

Run Test 33b until CIP_2 has path set

Operator initiates Ion_Exc_5 Shutdown

CIP_2 should shutdown automatically

3.	Start with:

Ion_Exc_6 Online/Recycle

Run Test 33c until CIP_2 has path set

Operator initiates Ion_Exc_6 Shutdown

CIP_2 should shutdown automatically