Test Plan – Rev 1

1.	Test Truck Wet Ingredient Unload Unit

(if by itself, disable read of blend and rail wet and set tank levels and rail wet indications from FT View or RSLogix)

a.	Operator initiates Shutdown

b.	Test one transfer

Set LI2110 to 0

Operator initiates Truck Transfer to T-2110. Specify truck station 1. Appropriate devices started and opened.

Set FI1148 to 200 (gpm)

Check that FQI1148 increasing

Wait awhile

Set LI2110 to 96

Auto-start shutdown of truck wet ingredient unload. Devices stopped properly

c.	Test other transfers

Set LI2140 to 50

Operator initiates another transfer (e.g., Truck Transfer to T-2140) Specify truck station 2. Proper devices started and opened.

Set FI1148 to 2 gpm

Auto-start Shutdown.

Repeat with another transfer.

d. 	Test Flush

Operator Initiate Flush

Manipulates appropriate valves

Eventually, auto-start Initiates Shutdown

e.	Test Hold and E-shutdown

Operator initiates Truck Transfer to T-2140.

Wait for a few devices to start

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves in the wrong position)

### Operator initiates Truck Transfer to T-2140 and check that devices in correct state.

Operator initiates E-Shutdown from screen

f.	Test failures cause Hold

Operator initiate Truck Transfer to T-2130

Cause a failure on a valve or pump. Verify goes into Hold

### Clear the failure and reset alarms

Operator initiate E-Shutdown

2.	Test Rail Wet Ingredient Unload Unit

(if by itself, disable read of blend and truck wet and set tank levels and truck wet indications from FT View or RSLogix)

a.	Operator initiates Shutdown

b.	Test one transfer

Set LI2120 to 0

Operator initiates Rail Transfer to T-2120. Specify rail station 1. Appropriate devices started and opened.

Set FI1198 to 200 (gpm)

Check that FQI1198 increasing

Wait awhile

Set LI2120 to 96

Auto-start shutdown of rail wet ingredient unload. Devices stopped properly

c.	Test other transfers

Set LI2130 to 50

Operator initiates another transfer (e.g., Rail Transfer to T-2130) Specify rail station 2. Proper devices started and opened.

Set FI1198 to 2 gpm

Auto-start Shutdown.

Repeat with another transfer.

d. 	Test Flush

Operator Initiate Flush

Manipulates appropriate valves

Eventually, auto-start Initiates Shutdown

e.	Test Hold and E-shutdown

Operator initiates Rail Transfer to T-2140.

Wait for a few devices to start

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves in the wrong position)

### Operator initiates Rail Transfer to T-2140 and check that devices in correct state.

Operator initiate E-Shutdown

f.	Test failures cause Hold

Operator initiate Rail Transfer to T-2120

Cause a failure on a valve or pump. Verify goes into Hold

### Clear the failure and reset alarms

Operator initiate E-Shutdown

3.	Test Dry Additive Unit (without Blend)

a.	Operator initiate Shutdown

b.	Test make-up

Set LI2150 to 0

Set LI2160 to 0

Operator initiates Makeup. Set destination to T-2150. 100 gallons of water. Devices started properly.

Check that FIC1320.PV is non zero and FQI1320 is increasing

Set FQI1320, LI3100 as needed

Auto-start of Shutdown initiated. Devices stopped properly

c.	Test make-up to other tank

Set LI2150 to 0

Set LI2160 to 0

Operator initiates Makeup. Set destination to T-2160. 200 gallons of water. Devices started properly.

Set FQI1320, LI3100 as needed

Auto-start of Shutdown initiated. Devices stopped properly

d.	Test flush

Operator Initiate flush

Devices started properly.

Auto-start Shutdown initiated. Devices stopped properly

d.	Test hold and E-shutdown

Operator initiates Flush.

Wait until flush time starts

Operator Initiate Hold from screen and verify that devices can be manipulated

(Close XV1312 and stop P-1310)

### Operator initiates Flush and check that XV13122 open and P-1310 running.

Initiate E-Shutdown

e.	Test failures cause Hold, Shutdown, or E-Shutdown

Operator Initiate Makeup. Wait for A-1300 to start

Cause a failure on A-1300. Verify goes into Hold

### Clear the failure and reset alarms

Operator Initiate Makeup. Wait for C-1300 to start

Cause a failure on conveyor. Verify goes into Shutdown

### Clear the failure and reset alarms

Operator Initiate Makeup. Wait for C-1300 to start

Set AS1302 to cause a belt alignment failure on conveyor. Verify goes into E-Shutdown

### Clear the failure and reset alarms

4.	Test Wet Additive Unit (without Blend) [not done 20xx]

5. Test Soda ash (by itself) – Already done

a.	Initiate shutdown

b.	Operator initiate Start Transfer.  Observe that devices closed/opened as necessary

c.	Test hold and E-Shutdown

Operator initiates Start Transfer

Wait awhile

Initiate Hold from screen and verify that devices can be manipulated

(Leave some devices in off state)

Operator initiates Start Transfer and check that appropriate devices turned on

Initiate E-Shutdown

d.	Test failures cause hold

Initiate Start Transfer

Cause a failure on a motor. Verify goes into Hold

### Clear the failure and reset alarms

Initiate E-Shutdown

6. Test CIP_1 (using soda ash)

a.	Operator Initiate shutdown

b.	Check Online/Recycle

Set LI6000 to 80

Operator initiate Online/Recycle.  Observe that devices closed/opened as necessary

c.	Test hold and E-Shutdown

Set LI6000 to 80

Operator initiates Online/Recycle.

Wait awhile

Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator initiates Online/Recycle and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Online/Recycle

Cause a failure on a valve or pump. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

e.	Check Waste/Make-up (Soda ash unit must be tested first)

Set LI6000 to 70

Set AI6000 to 7

Operator Initiate To Waste Tank

Wait awhile

# Set LI6000 to 1. Eventually, Make-up initiated

Set LI6000 as needed make sequence progress.

Check that FQI6050 increments when hot water flowing.

Soda ash unit transfer unit operates

Set AI6000 as needed to make sequence progress

### Online/recycle initiated automatically

f.	Check Product Storage path

Operator initiates Product Storage Path (from CIP_1 unit)

Appropriate valves opened/closed at correct time

At end, stays in last step

Operator initiates Online/Recycle (from CIP_1 unit)

g.	Check Ion Exchange path

Operator initiates Ion Exchange Path (from CIP_1 unit)

Appropriate valves opened/closed at correct time

At end, stays in last step

Operator initiates Online/Recycle (from CIP_1 unit)

h.	Check Reactor 1 path

Operator initiates Reactor 1 Path (from CIP_1 unit)

Appropriate valves opened/closed at correct time

At end, stays in last step

Operator initiates Online/Recycle (from CIP_1 unit)

i.	Check Reactor 2 path

Operator initiates Reactor 2 Path (from CIP_1 unit)

Appropriate valves opened/closed at correct time

At end, stays in last step

Operator initiates Online/Recycle (from CIP_1 unit)

7. Test QA Sampling [not done in 20xx]

(If reactor 1 and/or 2 not functional, disable message and set/clear indications manually)

a.	Operator Initiate shutdown

b.	Test Sample Reactor 1 start up

Set FI6310 to 1.0

Operator initiates Sample Reactor 1. Check that appropriate devices turned on, AI6300 settles out.

Check that signal to Reactor 1 unit turned on.

Eventually, XV6316 open and XV6315 closed.

c.	Test hold and E-Shutdown

Operator initiates Sample Reactor 1. Check that appropriate devices turned on, AI6300 settles out.

Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator initiates Sample Reactor 1. Check that appropriate devices turned on, AI6300 settles out.

Operator Initiate E-Shutdown

d.	Test failures causing hold

Initiate Sample Reactor 1.

Cause a failure on a valve or pump. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

e.	Test failures causing shutdown

Set FI6310 to 1.0

Operator initiates Sample Reactor 1. Check that appropriate devices turned on.

Set FI6310 to 0.05. Shutdown should auto-start initiate in 60 seconds.

f.	Test Lock Reactor 1 start up (by itself)

Set FI6310 to 1.0

Operator initiates Lock Reactor 1. Check that appropriate devices turned on, AI6300 settles out.

Check that signal to Reactor 1 unit turned on.

Eventually, XV6316 open and XV6315 closed.

g.	Test Lock Reactor 1 start up (after sampling already started)

Set FI6310 to 1.0

Operator initiates Sample Reactor 1. Check that appropriate devices turned on, AI6300 settles out.

Check that signal to Reactor 1 unit turned on.

Operator initiates Lock Reactor 1. Check that step # changes appropriately.

Check that lock signal to Reactor 1 unit turned on.

Eventually, XV6316 open and XV6315 closed.

Operator initiates Unlock Reactor 1. Check that shutdown auto-start initiated.

h.	Test Sample for Reactor 2 start up

Set FI6320 to 1.0

Operator initiates Sample Reactor 2. Check that appropriate devices turned on, AI6300 settles out.

Check that signal to Reactor 2 unit turned on.

Eventually, XV6326 open and XV6325 closed.

i.	Test Lock Reactor 2 start up (after sampling already started)

Set FI6320 to 1.0

Operator initiates Sample Reactor 2. Check that appropriate devices turned on, AI6300 settles out.

Check that signal to Reactor 2 unit turned on.

Operator initiates Lock Reactor 2. Check that step # changes appropriately.

Check that lock signal to Reactor 2 unit turned on.

Eventually, XV6326 open and XV6325 closed.

Operator initiates Unlock Reactor 2. Check that shutdown auto-start initiated.

j.	Test Flush R1 Path start up

Set FI6310 to 1.0

Operator initiates Flush R1 Path. Check that appropriate devices turned on.

After 5 minutes, shutdown initiated.

k.	Test Flush R2 Path start up

Set FI6320 to 1.0

Operator initiates Flush R2 Path. Check that appropriate devices turned on.

After 5 minutes, shutdown auto-start initiated.

8. Test Blend Unit

(If reactor 1 and/or 2 not functional, disable message and set/clear indications manually)

a.	Operator Initiate shutdown

b.	Test Blend for Reactor 1 start up

Set LI2110, LI2120, LI2130 to 40 (40 % full)

Set FY3002 to 0.60

Set FY3003 to 0.20

Operator initiates Blend for Reactor 1. Check that appropriate devices turned on, blend flows started and XV3011 open.

Check that FQI3001, FQI3002, FQI3003 are increasing.

Check that signal to Reactor 1 unit turned on

c.	Test hold and E-Shutdown

Set LI2110, LI2120, LI2130 to 40

Operator initiates Blend for Reactor 1. Check that appropriate devices turned on, blend flows started and XV3011 open.

Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator initiates Blend for Reactor 1. Check that appropriate devices turned on, blend flows started and XV3011 open.

Operator Initiate E-Shutdown

d.	Test failures causing hold

Initiate Blend for Reactor 1.

Cause a failure on a valve or pump. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

e.	Test failures causing shutdown

Set LI2110, LI2120, LI2130 to 40

Set FY3002 to 0.50

Operator initiates Blend for Reactor 1. Check that appropriate devices turned on, blend flows started and XV2512 open.

Check that signal to Batch unit turned on

Set LI2120 to 4. Shutdown should initiate in 20 seconds.

f.	Test Blend for Reactor 2 start up

Set LI2110, LI2120, LI2130 to 40

Set FY3002 to 0.60

Set FY3003 to 0.0

Operator initiates Blend for Reactor 2. Check that appropriate devices turned on, blend flows started and XV3012 open

Check that signal to Reactor 2 unit turned on

9.	Test Reactor 1 Unit (without CIP_1)

(If blend and/or ion exchange not functional, disable message and set/clear indications manually)

a.	Operator Initiate shutdown

b.	Test one cycle

Make sure Ion Exchange 1 is Online

Set LI3100 to 0

Operator initiates Make Batch. Set FI3101 to 500. Check that FQI3101and FQI3102 increasing at appropriate steps. Set FQI3101, FQI3102 and LI3100 as needed to make sequence progress. Blend Unit should be requested to blend and shutdown at the appropriate times.

Set LI3100 to 0 when it is emptying reactor.

Rinse should be initiated. After XV3110 open, set FI3110 to 1000. FQI3110 should be increasing. Set LI3100 as needed to make sequence progress

Eventually, goes to shutdown automatically with auto-start

c.	Test hold and E-Shutdown

Set LI3100 to 0

Operator initiates Make Batch.

Wait awhile

Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

### Operator initiates Make Batch and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Make Batch

Cause a failure on a valve or pump. Verify goes into Hold

### Clear the failure and reset alarms

Operator Initiate E-Shutdown

10.	Test Ion Exchange 1 (without CIP_1)

a.	Operator Initiate shutdown

b.	Test one cycle

Set AI4100 to 40 (40 mmho/cm)

Set FQI4101 to 0

Set FQI4102 to 0

Set FQI4103 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online automatically initiated.

Set FI4101 to 200

Check that FQI4101 increasing

Wait awhile

Set FQI4101 to 100,000

Check that regenerating sequence starts (reactor must not be in  Make Batch sequence)

Set FQI4102 and FQI4103 as needed to make sequence progress

Eventually, goes to shutdown automatically with auto-start

c.	Test hold and E-Shutdown

Set AI4100 to 40 (40 mmho/cm)

Set FQI4101 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online   automatically initiated.

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator initiates Startup and check that appropriate devices turned off  or on and Online automatically initiated

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Startup, eventually to Online automatically with auto-start

Cause a failure on a valve or pump. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

### Operator Initiate Startup, eventually to Online

11.	Test Storage Tank 1 unit (without CIP_1)

a.	Operator Initiate shutdown

b.	Set LI5100 to 50 (50% full)

Set LI5110 to 3

Operator Start Transfer to T5110 and check that appropriate devices turned on

Wait awhile

Set LI5110 to 96

Check that sequence finishes and QA tank system shutdown automatically (auto-start)

c.	Repeat b for transfer to T5120, except set LI5000 to 2 to finish

d.	Repeat b for transfer to T5130

e.	Repeat b except test hold and E-Shutdown

Set LI5100 to 50 (50% full)

Set LI5110 to 3

Operator Start Transfer to T5110 and check that appropriate devices turned on

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Start Transfer to T5110 and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

f.	Test failures cause hold

Operator Start Transfer to T5130 and check that appropriate devices turned on

Cause a failure on XV5131. Verify goes into Hold

### Clear the failure and reset alarms

Operator Initiate E-Shutdown

12.	Test storage loadout 1 unit

a.	Operator Initiate shutdown

b.	Set LI5110 to 50 (50% full)

Start T5110 Transfer and check that appropriate devices turned on

Wait awhile

## Set LI5110 to 2

Check that sequence finishes and loadout system shutdown automatically (auto-start)

c.	Repeat b for T5120 transfer

d.	Repeat b for T5130 transfer

e.	Set LI5120 to 10 (10% full)

Set amount to transfer to 400

Start T5120 Transfer and check that appropriate devices turned on

When FQI5181 becomes 400, check that sequence finishes and loadout system shutdown automatically (auto-start)

f.	Repeat b except test hold and E-Shutdown

Set LI5110 to 50 (50% full)

Operator Start T5110 Transfer and check that appropriate devices turned on

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Start T5110 Transfer and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

g.	Test failures cause hold

Operator Start T5110 Transfer and check that appropriate devices turned on

Cause a failure on XV5112. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

13. Test CIP_1 (with everything others)

a.	Operator Initiate Online/Recycle

b.	Storage Tank 1 flush check

Set LI5000 to 40

Set LI5130 to 30

Operator Initiate Storage Tank 1 unit Flush (from Stor_Tnk_1 unit)

Appropriate valves opened/closed at correct time, CIP Product Storage Path auto-started at appropriate time and then CIP_1 Online/Recycle auto-started at appropriate time

c.	Ion Exchange 1 flush check

Operator Initiate Ion Exchange 1 unit Flush (from Ion_Exc_1)

Appropriate valves opened/closed at correct time, CIP_1 Ion Exchange Path auto-started at appropriate time and then CIP_1 Online/Recycle auto-started at appropriate time

d.	Ion Exchange 2 flush check

Operator Initiate Ion Exchange 2 unit Flush (from Ion_Exc_2)

Appropriate valves opened/closed at correct time, CIP_1 Ion Exchange Path auto-started at appropriate time and then CIP_1 Online/Recycle auto-started at appropriate time

e.	Reactor 1 Flush check

Operator Initiate Reactor 1 unit Flush (from React_1)

Appropriate valves opened/closed at correct time, CIP_1 Reactor 1 Path auto-started at appropriate time and then CIP_1 Online/Recycle auto-started at appropriate time

f.	Reactor 2 Flush check

Operator Initiate Reactor 2 unit Flush (from React_2)

Appropriate valves opened/closed at correct time, CIP_1 Reactor 2 Path auto-started at appropriate time and then CIP_1 Online/Recycle auto-started at appropriate time

14.	Test Dry Storage Load In Unit (without Rail Dry Unload or Truck Dry Unload)

a.	Operator Initiate LoadIn Shutdown

b.	Test one cycle

Set LI2210 to 0

Set LI2230 to 0

Set LI2250 to 0

Operator initiates Start Path to T-2210. Devices started and positioned properly.

Operator initiates LoadIn Shutdown. Devices stopped properly

c.	Test other transfers in

Set LI2210 to 50

Set LI2230 to 50

Set LI2250 to 50

Operator initiates Start Path to T-2230. Devices started and positioned properly.

Operator initiates LoadIn Shutdown.

Operator initiates Start Path to T-2250. Devices started and positioned properly.

Operator initiates LoadIn Shutdown.

d.	Test LoadIn hold and LoadIn E-shutdown

Operator initiates Start Path to T-2250.

Wait for a few devices to start

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave all flop gates in the wrong position)

### Operator initiates Start Path to T-2250 and check that flop gates placed in correct position.

Operator Initiate LoadIn E-Shutdown

e.	Test failures cause LoadIn Shutdown or LoadIn E-Shutdown

Operator Initiate Start Path to T-2250

Cause a failure on a conveyor. Verify goes into LoadIn E-Shutdown

### Clear the failure and reset alarms

15.	Test Rail Dry Ingredient Unload Unit

(if testing without Dry Storage Load In operational, disable read of dry storage and set tank levels from FT View or RSLogix, and manually set transfer running indication)

a.	Operator Initiate Shutdown

b.	Test one cycle

Set LI2210 to 0

Set LI2230 to 0

Set LI2250 to 0

Operator initiates Start Rail Transfer to T-2210. Specify right rail dump. Initiates correct path from Dry Storage Load In unit. Devices started and positioned properly.

Set LI2210 to 96.  Initiates shutdown of dry storage load in. Devices stopped properly

c.	Test other transfers

Set LI2210 to 50

Operator initiates another transfer (e.g., Start Rail Transfer to T-2230) Specify left rail dump. Devices started and positioned properly.

Operator initiates Shutdown.

Repeat with another transfer.

d.	Test Hold and E-shutdown

Operator initiates Start Rail Transfer to T-2250.

Wait for a few devices to start

Initiate Hold from screen and verify that devices can be manipulated

(Leave all flop gates in the wrong position)

### Operator initiates Start Rail Transfer to T-2250 and check that devices in correct state.

Operator Initiate E-Shutdown

e.	Test failures cause Shutdown or E-Shutdown

Operator Initiate Start Rail Transfer to T-2230

Cause a failure on a conveyor. Verify goes into E-Shutdown

### Clear the failure and reset alarms

16.	Test Truck Dry Ingredient Unload Unit

(if testing without Dry Storage Load In operational, disable read of dry storage and set tank levels from FT View or RSLogix, and manually set transfer running indication)

a.	Operator Initiate Shutdown

b.	Test one cycle

Set LI2210 to 0

Set LI2230 to 0

Set LI2250 to 0

Operator initiates Start Truck Transfer to T-2210.Initiates correct path from Dry Storage Load In unit. Devices started and positioned properly.

Set LI2210 to 96.  Initiates shutdown of dry storage load in. Devices stopped properly

c.	Test other transfers

Set LI2210 to 50

Operator initiates another transfer (e.g., Start Truck Transfer to T-2230). Devices started and positioned properly.

Operator initiates Shutdown.

Repeat with another transfer.

d.	Test Hold and E-shutdown

Operator initiates Start Truck Transfer to T-2250.

Wait for a few devices to start

Initiate Hold from screen and verify that devices can be manipulated

(Leave all flop gates in the wrong position)

### Operator initiates Start Truck Transfer to T-2250 and check that devices in correct state.

Operator Initiate E-Shutdown

e.	Test failures cause Shutdown or E-Shutdown

Initiate Start Truck Transfer to T-2230

Cause a failure on a conveyor. Verify goes into E-Shutdown

### Clear the failure and reset alarms

17.	Test Dry Storage Load Out Unit

a.	Initiate LoadOut Shutdown

b.	Test one cycle

Set LI2210 to 50 (in Dry Unload)

Set LI2230 to 50 (in Dry Unload)

Set LI2250 to 50 (in Dry Unload)

Operator initiates Start Path from T-2210. Devices started properly.

Operator initiates LoadOut Shutdown. Devices stopped properly

c.	Test other transfers

Operator initiates Start Path from T-2230. Devices started properly.

Operator initiates LoadOut Shutdown.

Operator initiates Start Path from T-2250. Devices started properly.

Operator initiates LoadOut Shutdown.

d.	Test LoadOut hold and LoadOut E-shutdown

Operator initiates Start Path from T-2250.

Operator Initiate Hold from screen and verify that devices can be manipulated

### Operator initiates Start Path from T-2250 and check that devices in proper state.

Operator Initiate LoadOut E-Shutdown

e.	Test failures cause LoadOut Shutdown or LoadOut E-Shutdown

Operator Initiate Start Path from T-2210

Cause a failure on C-2290. Verify goes into LoadOut E-Shutdown

### Clear the failure and reset alarms

Operator Initiate Start Path from T-2230

Cause a failure on L-2239. Verify goes into LoadOut Shutdown

### Clear the failure and reset alarms

18.	Test Reactor 2 Unit (without CIP_1)

(If dry storage, blend, and/or ion exchange not functional, disable message and set/clear indications manually)

a.	Operator Initiate shutdown

b.	Test one cycle

Make sure Ion Exchange 2 is Online

Set LI3200 to 0

Set AI3200 to 8.0

Operator initiates Make Batch. Set FI3201 and FI3250  to 500. Check that FQI3201and FQI3250 increasing at appropriate steps. Set FQI3201 and AI3200 as needed to make sequence progress. Blend Unit should be requested to blend and shutdown at the appropriate times. Path from T-2210 should be set and loadout from dry ingredient storage should be started and shutdown at appropriate times.

Set LI3200 to 0 when it is emptying reactor.

Rinse should be initiated. After XV3210 open, set FI3210 to 1000. FQI3210 should be increasing. Set LI3200 as needed to make sequence progress

Eventually, goes to shutdown automatically with auto-start

c.	Test hold and E-Shutdown

Set LI3200 to 0

Operator initiates Make Batch.

Wait awhile

Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

### Operator initiates Make Batch and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Make Batch

Cause a failure on a valve or pump. Verify goes into Hold

### Clear the failure and reset alarms

Operator Initiate E-Shutdown

19.	Test Ion Exchange 2 (without CIP_1)

a.	Operator Initiate shutdown

b.	Test one cycle

Set AI4200 to 40 (40 mmho/cm)

Set FQI4201 to 0

Set FQI4202 to 0

Set FQI4203 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online automatically initiated.

Set FI4201 to 200

Check that FQI4201 increasing

Wait awhile

Set FQI4201 to 100,000

Check that regenerating sequence starts (reactor must not be in  Make Batch sequence)

Set FQI4202 and FQI4203 as needed to make sequence progress

Eventually, goes to shutdown automatically with auto-start

c.	Test hold and E-Shutdown

Set AI4200 to 40 (40 mmho/cm)

Set FQI4201 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online   automatically initiated.

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator initiates Startup and check that appropriate devices turned off or on and Online automatically initiated

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Startup, eventually to Online automatically

Cause a failure on a valve or pump. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

### Operator Initiate Startup, eventually to Online automatically

20.	Test Truck Powder Unload Unit

(if by itself, disable read of tank levels and set tank level indications from FT View or RSLogix)

a.	Operator Initiate Shutdown

b.	Test one transfer

Set LI2610 to 0

Operator initiates Transfer. Specifies Destination as T-2610 and source as truck station 1. Appropriate devices started and opened.

Set FI2448 to 200 (lbs/min)

Check that FQI2448 is increasing

Wait awhile

Set LI2610 to 96

Auto-start Initiates shutdown of truck powder unload. Devices stopped properly

c.	Test other transfers

Set LI2640 to 50

Operator initiates another transfer. Destination is T-2640 and source is truck station 2. Proper devices started and opened.

Set FI2448 to 2 lbs/min

Auto-start Initiates Shutdown.

Repeat with another transfer.

d. 	Test Filter Clean

Initiate Filter Clean

Manipulates appropriate valves

Auto-start Initiates Shutdown

e.	Test Hold and E-shutdown

Operator initiates Truck Transfer to T-2640.

Wait for a few devices to start

Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves in the wrong position)

### Operator initiates Truck Transfer to T-2640 and check that devices in correct state.

Operator Initiate E-Shutdown

f.	Test failures cause Hold

Operator Initiate Truck Transfer to T-2630

Cause a failure on a valve or pump. Verify goes into Hold

### Clear the failure and reset alarms

Operator Initiate E-Shutdown

21.	Test Rail Powder Ingredient Unload Unit

(if by itself, disable read of tank levels and set tank level indications from FT View or RSLogix)

a.	Operator Initiate Shutdown

b.	Test one transfer

Set LI2620 to 0

Operator initiates Transfer. Specifies Destination as T-2620 and source as rail station 1. Appropriate devices started and opened.

Set FI2498 to 200 (lbs/min)

Check that FQI2498 is increasing

Wait awhile

Set LI2620 to 96

Auto-start Initiates shutdown of rail powder unload. Devices stopped properly

c.	Test other transfers

Set LI2630 to 50

Operator initiates another transfer. Destination is T-2630 and source is rail station 2. Proper devices started and opened.

Set FI2498 to 2 lbs/min

Auto-starts Initiates Shutdown.

Repeat with another transfer.

d. 	Test Filter Clean

Operator Initiate Filter Clean

Manipulates appropriate valves

Auto-start Initiates Shutdown

e.	Test Hold and E-shutdown

Operator initiates Rail Transfer to T-2640.

Wait for a few devices to start

Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves in the wrong position)

### Operator initiates Rail Transfer to T-2640 and check that devices in correct state.

Operator Initiate E-Shutdown

f.	Test failures cause Hold

Operator Initiate Rail Transfer to T-2620

Cause a failure on a valve or pump. Verify goes into Hold

### Clear the failure and reset alarms

Operator Initiate E-Shutdown

22.	Test Reactor 3 Unit

(If ion exchanges 3/4 not functional, disable message and set/clear indications manually)

a.	Operator Initiate shutdown

b.	Test one cycle

Make sure Ion Exchange 3 is Online

Set LI3300 to 0

Set AI3300 to 8.0

Operator initiates Make Batch. Powder from T-2610. Set FI3301 to 500. Check that FQI3301and FQI3302 increasing at appropriate steps. Set FQI3301 and AI3300 as needed to make sequence progress.

Set LI3300 to 0 when it is emptying reactor.

Rinse should be initiated. After XV3310 open, set FI3310 to 1000. FQI3310 should be increasing. Set LI3300 as needed to make sequence progress

Eventually, goes to shutdown automatically with auto-start

c.	Test hold and E-Shutdown

Set LI3300 to 0

Operator initiates Make Batch.

Wait awhile

Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

### Operator initiates Make Batch and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Make Batch

Cause a failure on a valve or pump. Verify goes into Hold

### Clear the failure and reset alarms

Operator Initiate E-Shutdown

23.	Test Ion Exchange 3

a.	Operator Initiate shutdown

b.	Test one cycle

Set AI4300 to 40 (40 mmho/cm)

Set FQI4301 to 0

Set FQI4302 to 0

Set FQI4303 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online automatically initiated.

Wait awhile

Set FI4301 to 200

Check that FQI4301 increasing

Set FQI4301 to 100,000

Check that regenerating sequence starts (reactor 3 must not be in  Make Batch sequence)

Set FQI4302 and FQI4303 as needed to make sequence progress

Eventually, goes to shutdown automatically with auto-start

c. 	Test Flush

Operator Initiate Flush

Manipulates appropriate valves

Auto-start Initiates Shutdown

d.	Test hold and E-Shutdown

Set AI4300 to 40 (40 mmho/cm)

Set FQI4301 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online   automatically initiated.

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator initiates Startup and check that appropriate devices turned off or on and online automatically initiated

Operator Initiate E-Shutdown

e.	Test failures cause hold

Operator Initiate Startup, eventually to Online automatically

Cause a failure on a valve or pump. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

### Operator Initiate Startup, eventually to Online automatically

24.	Test Ion Exchange 4

a.	Operator Initiate shutdown

b.	Test one cycle

Set AI4400 to 40 (40 mmho/cm)

Set FQI4401 to 0

Set FQI4402 to 0

Set FQI4403 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online automatically initiated.

Set FI4401 to 200

Check that FQI4401 increasing

Wait awhile

Set FQI4401 to 100,000

Check that regenerating sequence starts (reactor 3 must not be in Make Batch sequence)

Set FQI4402 and FQI4403 as needed to make sequence progress

Eventually, goes to shutdown automatically

c. 	Test Flush

Operator Initiate Flush

Manipulates appropriate valves

Auto-start Initiates Shutdown

d.	Test hold and E-Shutdown

Set AI4400 to 40 (40 mmho/cm)

Set FQI4401 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online   automatically initiated.

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator initiates Startup and check that appropriate devices turned off or on and Online automatically initiated

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Startup, eventually to Online automatically

Cause a failure on a valve or pump. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

### Operator Initiate Startup, eventually to Online automatically

25.	Test Storage Tank 2 unit

a.	Operator Initiate shutdown

b.	Set LI5200 to 50 (50% full)

Set LI5210 to 3

Operator Start Transfer to T5610 and check that appropriate devices turned on

Wait awhile

Set LI5210 to 96

Check that sequence finishes and QA tank system shutdown automatically (auto-start)

c.	Repeat b for transfer to T5220, except set LI5200 to 2 to finish

d.	Repeat b for transfer to T5230

e.	Repeat b except test hold and E-Shutdown

Set LI5200 to 50 (50% full)

Set LI5210 to 3

Operator Start Transfer to T5210 and check that appropriate devices turned on

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator Start Transfer to T5210 and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

f.	Storage Tank 2 flush check

Set LI5200 to 40

Set LI5230 to 30

Operator Initiate Flush

Appropriate valves opened/closed at correct time

Eventually, goes to shutdown automatically (auto-start)

g.	Test failures cause hold

Operator Start Transfer to T5230 and check that appropriate devices turned on

Cause a failure on XV5231. Verify goes into Hold

### Clear the failure and reset alarms

Operator Initiate E-Shutdown

26.	Test storage loadout 2 unit

a.	Operator Initiate shutdown

b.	Set LI5210 to 50 (50% full)

Start T5210 Transfer and check that appropriate devices turned on

Wait awhile

## Set LI5210 to 2

Check that sequence finishes and loadout system shutdown automatically (auto-start)

c.	Repeat b for T5220 transfer

d.	Repeat b for T5230 transfer

e.	Set LI5220 to 10 (10% full)

Set amount to transfer to 400

Operator Start T5220 Transfer and check that appropriate devices turned on

When FQI5281 becomes 400, check that sequence finishes and loadout system shutdown automatically (auto-start)

f.	Repeat b except test hold and E-Shutdown

Set LI5210 to 50 (50% full)

Operator Start T5210 Transfer and check that appropriate devices turned on

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Start T5210 Transfer and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

g.	Test failures cause hold

Operator Start T5210 Transfer and check that appropriate devices turned on

Cause a failure on XV5212. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

27.	Test Reactor 4 Unit

(If ion exchanges 5/6 not functional, disable message and set/clear indications manually)

a.	Operator Initiate shutdown

b.	Test one cycle

Make sure Ion Exchange 5 or 6 is Online

Set LI3400 to 0

Set AI3400 to 8.0

Operator initiates Make Batch. Gas from T-2810. Set FI3401 to 500. Check that FQI3401and FQI3402 increasing at appropriate steps. Set FQI3401 and AI3400 as needed to make sequence progress.

Set LI3400 to 0 when it is emptying reactor.

Rinse should be initiated. After XV3411 open, set FI3411 to 1000. FQI3411 should be increasing. Set LI3400 as needed to make sequence progress

Eventually, goes to shutdown automatically with auto-start

c.	Test hold and E-Shutdown

Set LI3400 to 0

Operator initiates Make Batch.

Wait awhile

Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

### Operator initiates Make Batch and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Make Batch

Cause a failure on a valve or pump. Verify goes into Hold

### Clear the failure and reset alarms

Operator Initiate E-Shutdown

28.	Test Ion Exchange 5 (without CIP_2)

a.	Operator Initiate shutdown

b.	Test one cycle

Set AI4500 to 40 (40 mmho/cm)

Set FQI4501 to 0

Set FQI4502 to 0

Set FQI4503 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online automatically initiated.

Set FI4501 to 200

Check that FQI4501 increasing

Wait awhile

Set FQI4501 to 100,000

Check that regenerating sequence starts (reactor 4 must not be in  Make Batch sequence)

Set FQI4502 and FQI4503 as needed to make sequence progress

Eventually, goes to shutdown automatically with auto-start

c.	Test hold and E-Shutdown

Set AI4500 to 40 (40 mmho/cm)

Set FQI4501 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online   automatically initiated.

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator initiates Startup and check that appropriate devices turned off  or on and Online automatically initiated

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Startup, eventually to Online automatically with auto-start

Cause a failure on a valve or pump. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

### Operator Initiate Startup, eventually to Online

29.	Test Ion Exchange 6 (without CIP_2)

a.	Operator Initiate shutdown

b.	Test one cycle

Set AI4600 to 40 (40 mmho/cm)

Set FQI4601 to 0

Set FQI4602 to 0

Set FQI4603 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online automatically initiated.

Set FI4601 to 200

Check that FQI4601 increasing

Wait awhile

Set FQI4601 to 100,000

Check that regenerating sequence starts (reactor 4 must not be in  Make Batch sequence)

Set FQI4602 and FQI4603 as needed to make sequence progress

Eventually, goes to shutdown automatically with auto-start

c.	Test hold and E-Shutdown

Set AI4600 to 40 (40 mmho/cm)

Set FQI4601 to 0

Operator initiates Startup. Check that appropriate devices turned on and Online   automatically initiated.

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator initiates Startup and check that appropriate devices turned off  or on and Online automatically initiated

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Startup, eventually to Online automatically with auto-start

Cause a failure on a valve or pump. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

### Operator Initiate Startup, eventually to Online

30.	Test Storage Tank 3 unit

a.	Operator Initiate shutdown

b.	Set LI5300 to 50 (50% full)

Set LI5310 to 3

Operator Start Transfer to T5610 and check that appropriate devices turned on

Wait awhile

Set LI5310 to 96

Check that sequence finishes and QA tank system shutdown automatically (auto-start)

c.	Repeat b for transfer to T5320, except set LI5300 to 2 to finish

d.	Repeat b for transfer to T5330

e.	Repeat b except test hold and E-Shutdown

Set LI5300 to 50 (50% full)

Set LI5310 to 3

Operator Start Transfer to T5310 and check that appropriate devices turned on

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator Start Transfer to T5310 and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

f.	Storage Tank 2 flush check

Set LI5300 to 40

Set LI5330 to 30

Operator Initiate Flush

Appropriate valves opened/closed at correct time

Eventually, goes to shutdown automatically (auto-start)

g.	Test failures cause hold

Operator Start Transfer to T5330 and check that appropriate devices turned on

Cause a failure on XV5331. Verify goes into Hold

### Clear the failure and reset alarms

Operator Initiate E-Shutdown

31.	Test storage loadout 3 unit

a.	Operator Initiate shutdown

b.	Set LI5310 to 50 (50% full)

Start T5310 Transfer and check that appropriate devices turned on

Wait awhile

## Set LI5310 to 2

Check that sequence finishes and loadout system shutdown automatically (auto-start)

c.	Repeat b for T5320 transfer

d.	Repeat b for T5330 transfer

e.	Set LI5320 to 10 (10% full)

Set amount to transfer to 400

Operator Start T5320 Transfer and check that appropriate devices turned on

When FQI5381 becomes 400, check that sequence finishes and loadout system shutdown automatically (auto-start)

f.	Repeat b except test hold and E-Shutdown

Set LI5310 to 50 (50% full)

Operator Start T5310 Transfer and check that appropriate devices turned on

Wait awhile

Operator Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Start T5310 Transfer and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

g.	Test failures cause hold

Operator Start T5310 Transfer and check that appropriate devices turned on

Cause a failure on XV5312. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

32. Test CIP_2 (by itself)

a.	Operator Initiate shutdown

b.	Check Online/Recycle

Set LI6200 to 80

Operator initiate Online/Recycle.  Observe that devices closed/opened as necessary

c.	Test hold and E-Shutdown

Set LI6200 to 80

Operator initiates Online/Recycle.

Wait awhile

Initiate Hold from screen and verify that devices can be manipulated

(Leave some valves open that should not be open)

Operator initiates Online/Recycle and check that appropriate devices turned off or on

Operator Initiate E-Shutdown

d.	Test failures cause hold

Operator Initiate Online/Recycle

Cause a failure on a valve or pump. Verify goes into Hold

Clear the failure and reset alarms

Operator Initiate E-Shutdown

e.	Check Waste/Make-up

Set LI6200 to 70

Set AI6200 to 7

Operator Initiate To Waste Tank

Wait awhile

# Set LI6200 to 1. Eventually, Make-up initiated

Set LI6200 as needed make sequence progress.

Set AI6200 as needed to make sequence progress

### Online/recycle initiated automatically

g.	Check Ion Exchange path

Operator initiates Ion Exchange Path (from CIP_2 unit)

Appropriate valves opened/closed at correct time

At end, stays in last step

Operator initiates Online/Recycle (from CIP_2 unit)

h.	Check Reactor 4 path

Operator initiates Reactor 1 Path (from CIP_2 unit)

Appropriate valves opened/closed at correct time

At end, stays in last step

Operator initiates Online/Recycle (from CIP_2 unit)

33. Test CIP_2 (with everything others)

a.	Operator Initiate Online/Recycle

b.	Ion Exchange 5 flush check

Operator Initiate Ion Exchange 1 unit Flush (from Ion_Exc_5)

Appropriate valves opened/closed at correct time, CIP_2 Ion Exchange Path auto-started at appropriate time and then CIP_2 Online/Recycle auto-started at appropriate time

c.	Ion Exchange 6 flush check

Operator Initiate Ion Exchange 2 unit Flush (from Ion_Exc_6)

Appropriate valves opened/closed at correct time, CIP_2 Ion Exchange Path auto-started at appropriate time and then CIP_2 Online/Recycle auto-started at appropriate time

d.	Reactor 4 Flush check

Operator Initiate Reactor 4 unit Flush (from React_4)

Appropriate valves opened/closed at correct time, CIP_2 Reactor 4 Path auto-started at appropriate time and then CIP_2 Online/Recycle auto-started at appropriate time