- K Process

- Control Narrative

Table of Contents

Process Overview	9

Truck Wet Unload Unit	10

Major Equipment	10

Analog Instrument and Control Point Listing	10

Discrete Instrument and Control Point Listing	10

Unit Operation Interactions	11

Truck Wet Unload Unit Operational States	11

Truck Wet Unload Abnormal Conditions	13

Rail Wet Unload Unit	14

Major Equipment	14

Analog Instrument and Control Point Listing	14

Discrete Instrument and Control Point Listing	14

Unit Operation Interactions	15

Rail Wet Unload Unit Operational States	15

Rail Wet Ingredient Unload Abnormal Conditions	17

Dry Additive Makeup Unit	18

Major Equipment	18

Analog Instrument and Control Point Listing	18

Discrete Instrument and Control Point Listing	18

Unit Operation Interactions	19

Dry Additive Makeup Unit Operational States	20

Dry Additive Makeup Abnormal Conditions	21

Wet Additive Makeup Unit	22

Major Equipment	22

Analog Instrument and Control Point Listing	22

Discrete Instrument and Control Point Listing	22

Unit Operation Interactions	24

Wet Additive Makeup Unit Operational States	24

Wet Additive Makeup Abnormal Conditions	25

Wet Ingredient Storage Unit	26

Major Equipment	26

Analog Instrument and Control Point Listing	26

Discrete Instrument and Control Point Listing	26

Unit Operation Interactions	28

Rail Dry Unload Unit	29

Major Equipment	29

Discrete Instrument and Control Point Listing	29

Unit Operation Interactions	31

Rail Dry Unload Unit Operational States	31

Rail Dry Ingredient Unload Unit Abnormal Conditions	32

Truck Dry Unload Unit	34

Major Equipment	34

Discrete Instrument and Control Point Listing	34

Unit Operation Interactions	36

Truck Dry Unload Unit Operational States	36

Truck Dry Unload Manual Control	37

Truck Dry Ingredient Unload Unit Abnormal Conditions	37

Dry Storage Loadin Unit	39

Major Equipment	39

Analog Instrument and Control Point Listing	39

Discrete Instrument and Control Point Listing	39

Unit Operation Interactions	40

Dry Storage Loadin Unit Operational States	41

Dry Storage Loadin Unit Abnormal Conditions	42

Dry Storage Loadout Unit	43

Major Equipment	43

Discrete Instrument and Control Point Listing	43

Unit Operation Interactions	43

Dry Storage Loadout Unit Operational States	44

Dry Storage Unit Abnormal Conditions	44

Truck Powder Unload Unit	46

Major Equipment	46

Analog Instrument and Control Point Listing	46

Discrete Instrument and Control Point Listing	46

Unit Operation Interactions	47

Truck Powder Unload Unit Operational States	47

Truck Powder Unload Abnormal Conditions	48

Rail Powder Unload Unit	50

Major Equipment	50

Analog Instrument and Control Point Listing	50

Discrete Instrument and Control Point Listing	50

Unit Operation Interactions	51

Rail Powder Unload Unit Operational States	51

Rail Powder Unload Abnormal Conditions	52

Powder Ingredient Storage Unit	54

Major Equipment	54

Analog Instrument and Control Point Listing	54

Discrete Instrument and Control Point Listing	54

Unit Operation Interactions	56

Gas Storage Unit	57

Major Equipment	57

Analog Instrument and Control Point Listing	57

Discrete Instrument and Control Point Listing	57

Unit Operation Interactions	58

Blend Unit	59

Major Equipment	59

Analog Instrument and Control Point Listing	59

Discrete Instrument and Control Point Listing	60

Unit Operation Interactions	61

Blend Unit Operational States	61

Blend Unit Abnormal Conditions	63

Reactor 1 Unit	64

Major Equipment	64

Analog Instrument and Control Point Listing	64

Discrete Instrument and Control Point Listing	65

Unit Operation Interactions	66

Reactor 1 Operational States	66

Reactor 1 Abnormal Conditions	69

Reactor 2 Unit	70

Major Equipment	70

Analog Instrument and Control Point Listing	70

Discrete Instrument and Control Point Listing	71

Unit Operation Interactions	72

Reactor 2 Operational States	72

Reactor 2 Abnormal Conditions	75

Reactor 3 Unit	76

Major Equipment	76

Analog Instrument and Control Point Listing	76

Discrete Instrument and Control Point Listing	77

Unit Operation Interactions	78

Reactor 3 Operational States	79

Reactor 3 Abnormal Conditions	81

Reactor 4 Unit	83

Major Equipment	83

Analog Instrument and Control Point Listing	83

Discrete Instrument and Control Point Listing	84

Unit Operation Interactions	85

Reactor 4 Operational States	85

Reactor 4 Abnormal Conditions	87

Note: "While making batch" means "after 1000 gal. water added and reactor level > 5% while product transferred out of reactor"	88

QA Sample Unit	89

Major Equipment	89

Analog Instrument and Control Point Listing	89

Discrete Instrument and Control Point Listing	89

Unit Operation Interactions	90

QA Sample Unit Operational States	90

QA Sampling Abnormal Conditions	93

Ion Exchange #1 Unit	94

Major Equipment	94

Analog Instrument and Control Point Listing	94

Discrete Instrument and Control Point Listing	95

Unit Operation Interactions	95

Ion Exchange #1 Unit Operational States	96

Ion Exchange #1 Abnormal Conditions	98

Ion Exchange #2 Unit	99

Major Equipment	99

Analog Instrument and Control Point Listing	99

Discrete Instrument and Control Point Listing	99

Unit Operation Interactions	100

Ion Exchange #2 Unit Operational States	101

Ion Exchange #2 Abnormal Conditions	103

Ion Exchange #3 Unit	104

Major Equipment	104

Analog Instrument and Control Point Listing	104

Discrete Instrument and Control Point Listing	104

Unit Operation Interactions	105

Ion Exchange #3 Unit Operational States	106

Ion Exchange #3 Abnormal Conditions	107

Ion Exchange #4 Unit	108

Major Equipment	108

Analog Instrument and Control Point Listing	108

Discrete Instrument and Control Point Listing	108

Unit Operation Interactions	109

Ion Exchange #4 Unit Operational States	110

Ion Exchange #4 Abnormal Conditions	111

Ion Exchange #5 Unit	112

Major Equipment	112

Analog Instrument and Control Point Listing	112

Discrete Instrument and Control Point Listing	113

Unit Operation Interactions	113

Ion Exchange #5 Unit Operational States	114

Ion Exchange #5 Abnormal Conditions	116

Ion Exchange #6 Unit	117

Major Equipment	117

Analog Instrument and Control Point Listing	117

Discrete Instrument and Control Point Listing	117

Unit Operation Interactions	118

Ion Exchange #6 Unit Operational States	119

Ion Exchange #6 Abnormal Conditions	120

Product Storage 1 Unit	122

Major Equipment	122

Analog Instrument and Control Point Listing	122

Discrete Instrument and Control Point Listing	122

Unit Operation Interactions	123

Product Storage 1 Operational States	123

Product Storage 1 Abnormal Conditions	124

Storage 1 Loadout Unit	126

Major Equipment	126

Analog Instrument and Control Point Listing	126

Discrete Instrument and Control Point Listing	126

Unit Operation Interactions	127

Storage 1 Loadout Unit Operational States	127

Storage 1 Loadout Abnormal Conditions	128

Product Storage 2 Unit	129

Major Equipment	129

Analog Instrument and Control Point Listing	129

Discrete Instrument and Control Point Listing	129

Unit Operation Interactions	130

Product Storage 2 Operational States	130

Product Storage 2 Abnormal Conditions	131

Storage 2 Loadout Unit	133

Major Equipment	133

Analog Instrument and Control Point Listing	133

Discrete Instrument and Control Point Listing	133

Unit Operation Interactions	134

Storage 2 Loadout Unit Operational States	134

Storage 2 Loadout Abnormal Conditions	135

Product Storage 3 Unit	136

Major Equipment	136

Analog Instrument and Control Point Listing	136

Discrete Instrument and Control Point Listing	136

Unit Operation Interactions	137

Product Storage 3 Operational States	137

Product Storage 3 Abnormal Conditions	139

Storage 3 Loadout Unit	140

Major Equipment	140

Analog Instrument and Control Point Listing	140

Discrete Instrument and Control Point Listing	140

Unit Operation Interactions	141

Storage 3 Loadout Unit Operational States	141

Storage 3 Loadout Abnormal Conditions	142

Clean-In-Place (CIP) 1 Unit	143

Major Equipment	143

Analog Instrument and Control Point Listing	143

Discrete Instrument and Control Point Listing	143

Unit Operation Interactions	144

CIP 1 Unit Operational States	145

CIP 1 Unit Abnormal Conditions	147

Soda Ash Unit	149

Major Equipment	149

Analog Instrument and Control Point Listing	149

Discrete Instrument and Control Point Listing	149

Unit Operation Interactions	150

Soda Ash Unit States	150

Soda Ash Abnormal Conditions	150

Clean-In-Place (CIP) 2 Unit	151

Major Equipment	151

Analog Instrument and Control Point Listing	151

Discrete Instrument and Control Point Listing	151

Unit Operation Interactions	152

CIP 2 Unit Operational States	153

CIP 2 Unit Abnormal Conditions	155

Revision History	156

# Process Overview

The K process represents a typical batch process. Dwg. 0001 presents an overall view of the process. It consists of 29 basic units divided into four areas. The loadin area consists of a wet unload cell, with truck wet and rail wet unload units (Dwg. 1001), and additive cell consisting of a dry additive makeup unit (Dwg. 1003) and a wet additive makeup unit (Dwg. 1004), a dry unload cell consisting of rail dry unload unit (Dwg. 2001), truck dry unload unit (Dwg. 2003), dry storage loadin, and dry storage loadout (Dwg. 2002), a powder unload cell consisting of truck and rail powder unload units (Dwg. 2004), and a gas ingredient unload unit (Dwg. 2007). The raw ingredients are unloaded from trucks and rail cars into storage tanks in the appropriate ingredient storage units. The wet ingredient storage (Dwg. 2001) is shared between the loadin area and production area. The powder storage (Dwg. 2006) is shared between the loading and production area. The gas storage (Dwg. 2008) is shared between the loading and production area. The production area is divided into a reactor and ion exchange cell. The reactor cell has a blending unit (Dwg. 3000) and four reactor units (Dwgs. 3001, 3002, 3003, and 3004), and a QA sample unit (Dwg. 3008). Certain ingredients are blended to produce one of the ingredients for two of the reactor units. Each reactor takes the appropriate ingredients from the blend and ingredient storage units and combines them to make a batch of product. The product is transferred though an ion exchanger to remove some impurities. The ion exchange cell (Dwgs. 4001, 4002, and 4003) has six ion exchangers. Ion exchangers 1 and 2 are for reactors 1 and 2. Ion exchangers 3 and 4 are for reactor 3. Ion exchangers 5 and 6 are for reactor 4. The ion exchangers are regenerated after a certain amount of product passes through the ion exchanger. The QA sample unit samples product from reactors 1 and 2 at the appropriate point in the reactor operation and presents the result to the operator so that he/she can decide how much, if any, additional reaction time is necessary. The loadout area consists of five units: a product storage 1 unit (Dwg 5001), a product storage 2 unit (Dwg. 5003), a product storage unit (Dwg. 5004) and a three loadout units (Dwg. 5002 and 5005). The product from an ion exchanger is initially stored in a QA tank before it is transferred to one of three storage tanks. From the storage tanks, it is transferred to a truck/rail loadout system. The utility area contains two clean-in-place (CIP) units (Dwg 6001 and 6002); and a QA sampling unit (Dwg. 3008). Each CIP unit has a tank and a recirculating loop that maintain the cleaning water temperature. The CIP 1 system (Dwg 6001) cleans out piping in the reactor 1, reactor 2, ion exchange 1, ion exchange 2 units and the product storage 1 unit. In the CIP 1 unit, soda ash and hot water are used to make up the cleaning water. The CIP 1 unit (Dwg 6002) cleans out piping in the reactor 4, ion exchange 5 and ion exchange 6 units. In the CIP 2 unit, liquid caustic and hot water are used to make up the cleaning water.

Note that the units could be divided differently. For example, the rail dry unload unit could be combined with the dry storage loadin unit and the dry storage loadout unit could be combined with reactor 2. The units are divided to provide projects that are approximately the same size. Details about the project teams are described in the project description document.

# Truck Wet Unload Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| P-1145 | Truck Unload Pump | Centrifugal pump that transfers liquid ingredient from one of two truck unload stations to truck unload header and to one of the wet ingredient storage tanks. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| FI1148 | Indicator | Truck unload header flow | Measure outflow of truck unload pump | 0-1000 gpm |  |
| FQI1148 | Indicator | Totalized truck unload transfer flow | Measure amount of ingredient transferred to tank |  |  |
| PI1111 | Indicator | XV1111 purge air pressure | Measure purge air pressure at truck unload station 1 | 0-100 psi |  |
| PI1121 | Indicator | XV1121 purge air pressure | Measure purge air pressure at truck unload station 2 | 0-100 psi |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-1145 | Pump | Truck Unload Pump | Pumps liquid from truck stations into truck unload header |  |
| XV1111 | Valve | Truck Station 1 Purge Air Valve | Allows purge air into truck trailer at truck station 1 |  |
| XV1112 | Valve | Truck Station 1 Unload Valve | Allows flow of wet ingredient from truck station 1 into pump |  |
| XV1121 | Valve | Truck Station 2 Purge Air Valve | Allows purge air into truck trailer at truck station 2 |  |
| XV1122 | Valve | Truck Station 2 Unload Valve | Allows flow of wet ingredient from truck station 2 into pump |  |
| XV1145 | Valve | Truck Unload Header Feed Valve | Allows flow of liquid from truck unload stations into truck unload header |  |
| XV1146 | Valve | Truck Cleaning Water Feed Valve | Allows flow of hot cleaning water into truck unload header |  |

Devices in Wet Ingredient Storage

| XV2111 | Valve | T-2110 Truck Feed Valve | Controls flow from truck unload header into T-2110 |  |
| --- | --- | --- | --- | --- |
| XV2121 | Valve | T-2120 Truck Feed Valve | Controls flow from truck unload header into T-2120 |  |
| XV2131 | Valve | T-2130 Truck Feed Valve | Controls flow from truck unload header into T-2130 |  |
| XV2141 | Valve | T-2140 Truck Feed Valve | Controls flow from truck unload header into T-2140 |  |
| XV2196 | Valve | Truck Header Drain Valve | Controls flow from truck unload header to drain |  |

## Unit Operation Interactions

Rail Wet Unload Unit Liquids unloaded from a truck trailer must not go into the same destination tank being used by the rail wet unload unit.

## Truck Wet Unload Unit Operational States

Note: The operator must select a source station and a destination tank.

	Transfer - Transfers the entire contents of the tank trailer at the selected truck unload station to the selected destination tank. Do not allow this operation to start if any Truck Transfer is in operation. Steps:

Display prompt for operator and operator selects source and destination

If destination tank is more than 80% full, abort operation (jump to last step)

If Rail Transfer to selected destination tank is in operation, abort operation

Close all valves (one step)

Initialize FQI1148

Open appropriate air purge valve (XV1111 or XV1121)

Open appropriate unload valve (XV1112 or XV1122)

Open XV1145

Open appropriate XV21x1

Start P-1145

Wait until destination tank is full (level > 95%), or low flow in truck unload header (flow < 10 gpm)

Shut down the system

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Flush - Flushes the truck unload header with hot water. Can only be requested if already shutdown

Open truck header water return valve XV2196

Open XV1146

Open XV1145

Start P-1145

Flush for 10 minutes

Shut down the system

	Shutdown - Turns off the pump and all valves:

Stop P-1145

Close XV1111

Close XV1112

Close XV1121

Close XV1122

Close XV1145

Close XV1146

Close XV2111

Close XV2121

Close XV2131

Close XV2141

Close XV2196

	E-Shutdown - Immediately turns off the pump and all storage header valves:

Stop P-1145

Close XV1111, XV1112, XV1121, XV1122, XV1145, XV1146, XV2111, XV2121, XV2131, XV2141, XV2196

### Truck Wet Unload Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

PI1111 < 10 psi and XV1111 open 5 seconds  Alarm

PI1121 < 10 psi and XV1121 open 5 seconds  Alarm

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Rail Wet Unload Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| P-1195 | Rail Unload Pump | Centrifugal pump that transfers liquid ingredient from one of two rail unload stations to rail unload header and to one of the wet ingredient storage tanks. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| FI1198 | Indicator | Rail unload header flow | Measure outflow of rail unload pump | 0-1000 gpm |  |
| FQI1198 | Indicator | Totalized rail car unload transfer flow | Measure amount of ingredient transferred to tank |  |  |
| PI1151 | Indicator | XV1151 purge air pressure | Measure purge air pressure at rail unload station 1 | 0-100 psi |  |
| PI1161 | Indicator | XV1161 purge air pressure | Measure purge air pressure at rail unload station 2 | 0-100 psi |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-1195 | Pump | Rail Unload Pump | Pumps liquid from rail stations into rail unload header |  |
| XV1151 | Valve | Rail Station 1 Purge Air Valve | Allows purge air into railcar at rail station 1 |  |
| XV1152 | Valve | Rail Station 1 Unload Valve | Allows flow of wet ingredient from rail station 1 into pump |  |
| XV1161 | Valve | Rail Station 2 Purge Air Valve | Allows purge air into railcar at rail station 2 |  |
| XV1162 | Valve | Rail Station 2 Unload Valve | Allows flow of wet ingredient from rail station 2 into pump |  |
| XV1195 | Valve | Rail Unload Header Feed Valve | Allows flow of liquid from rail unload stations into rail unload header |  |
| XV1196 | Valve | Rail Cleaning Water Feed Valve | Allows flow of hot cleaning water into rail unload header |  |

Devices in Wet Ingredient Storage

| XV2112 | Valve | T-2110 Rail Feed Valve | Controls flow from rail unload header into T-2110 |  |
| --- | --- | --- | --- | --- |
| XV2122 | Valve | T-2120 Rail Feed Valve | Controls flow from rail unload header into T-2120 |  |
| XV2132 | Valve | T-2130 Rail Feed Valve | Controls flow from rail unload header into T-2130 |  |
| XV2142 | Valve | T-2140 Rail Feed Valve | Controls flow from rail unload header into T-2140 |  |
| XV2198 | Valve | Rail Header Drain Valve | Controls flow from rail unload header to drain |  |

## Unit Operation Interactions

Truck Wet Unload Unit Liquids unloaded from a rail car must not go into the same destination tank being used by the truck wet unload unit.

## Rail Wet Unload Unit Operational States

Note: The operator must select a source station and a destination tank.

	Transfer - Transfers the entire contents of the tankcar at the selected rail unload station to the selected destination tank. Do not allow this operation to start if any Rail Transfer is already in operation. Steps:

Display prompt for operator and operator selects source and destination

If destination tank is more than 80% full, abort operation (jump to last step)

If Truck Transfer to selected destination tank is in operation, abort operation

Close all valves (one step)

Initialize FQI1198

Open appropriate air purge valve (XV1151 or XV1161)

Open appropriate unload valve (XV1152 or XV1162)

Open XV1195

Open XV21x2

Start P-1195

Wait until destination tank is full (level > 95%), or low flow in rail unload header (flow < 10 gpm)

Shut down the system

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Flush - Flushes the rail unload header with hot water. Can only be requested if already shutdown.

Open rail header water return valve XV2198

Open XV1196

Open XV1195

Start P-1195

Flush for 10 minutes

Shutdown

	Shutdown - Turns off the pump and all valves:

Stop P-1195

Close XV1151

Close XV1152

Close XV1161

Close XV1162

Close XV1195

Close XV1196

Close XV2112

Close XV2122

Close XV2132

Close XV2142

Close XV2198

	E-Shutdown - Immediately turns off the pump and all storage header valves:

Stop P-1195

Close XV1151, XV1152, XV1161, XV1162, XV1195, XV1196, XV2112, XV2122, XV2132, XV2142, XV2198

### Rail Wet Ingredient Unload Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

PI1151 < 10 psi and XV1151 open 5 seconds  Alarm

PI1161 < 10 psi and XV1161 open 5 seconds  Alarm

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Dry Additive Makeup Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-1300 | Mix Tank agitator | Mix the additive into water |
| P-1310 | Mix Tank Unload Pump | Centrifugal pump that transfers liquid additive to dry additive header and to one of the additive ingredient storage tanks. |
| T-1300 | Additive Mix Tank | 500 gallon tank. Dry additive is mixed in tank and is transferred from this tank. |
| C-1301 | Additive Conveyor | Conveys additive from the material addition hopper to the slide gate. |
| G-1300 | Additive Tank Slide Gate | Additive enters the mix tank through this gate. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI1300 | Indicator | pH of Mix Tank | Monitor pH to determine proper make-up | 0-14 |  |
| FIC1320 | Loop | Hot water supply flow control | Controls feed rate of hot water to Mix tank | 0-50 gpm, Fail closed, direct acting |  |
| FQI1320 | Indicator | Totalized hot water flow | Measures amount of hot water placed into mix tank |  |  |
| LI1300 | Indicator | Level of Mix Tank | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-1300 | Motor | Mix tank agitator | Mixes water and additive in mix tank |  |
| C-1301 | Conveyor | Ingredient Conveyor | Moves ingredient from hopper to mix tank slide gate. |  |
| M-1300 | Motor | Mix Tank Slide Gate Motor | Opens/closes mix tank slide gate |  |
| P-1310 | Pump | Mix Tank Unload Pump | Pumps liquid from mix tank into dry additive header |  |
| SS1301 | Speed Switch | C-1301 Speed Switch | Indicates that conveyor is stopped |  |
| XV1311 | Valve | Mix Tank Outlet Valve | Allows flow of additive from mix tank into pump |  |
| XV1312 | Valve | Dry Mix Unload Valve | Allows flow of liquid from pump into dry mix header |  |
| XV1313 | Valve | Hot water supply Valve | Allows flow of hot cleaning water into dry mix header |  |
| XV1314 | Valve | Drain Valve | Allows flow of liquid from pump to drain |  |
| XV1321 | Valve | Cold water supply Valve | Allows flow of cold water into mix tank |  |
| ZSC1300 | Limit Switch | ZS1300 slide gate switch | Indicates slide gate is closed |  |
| ZSO1300 | Limit Switch | ZS1300 slide gate switch | Indicates slide gate is open |  |

Devices in Wet Ingredient Storage

| XV2152 | Valve | T-2150 Dry Add Feed Valve | Controls flow from dry additive header into T-2150 |  |
| --- | --- | --- | --- | --- |
| XV2162 | Valve | T-2160 Dry Add Feed Valve | Controls flow from dry additive header into T-2160 |  |
| XV2194 | Valve | Dry Add Header Drain Valve | Controls flow from dry additive header to drain |  |

## Unit Operation Interactions

Wet Additive Makeup Unit Liquids unloaded from dry additive makeup must not go into the same destination tank being used by the wet additive makeup unit.

## Dry Additive Makeup Unit Operational States

Note: The operator must select a destination tank.

	Make-up - Makes up a new batch of additive from the hot water supply and bagged material from hopper, initiated by operator.

If Mix Tank level >= 2%, abort.

Display prompt for operator and operator selects destination

If Wet Additive to selected destination tank is in operation, abort operation

Close all valves (one step)

Initialize FQI1300

Request amount of hot water from operator

###### Wait for confirmation from operator

Put Hot Water Flow Controller FIC1320 in auto, setpoint = 40 gpm

Wait for amount of hot water

Start Agitator A-1300

Open Mix Tank Slide Gate G-1300

Start Mix Conveyor C-1300

Wait for operator confirmation that additive sample is okay

Stop Mix Conveyor C-1300

Close Mix Tank Slide Gate G-1300

Open appropriate XV21x1

Open Dry Mix Unload Valve XV1312

Open Mix Tank Outlet Valve XV1311

Start pump P-1310

Wait for Mix Tank level to be less than 1% for 30 seconds

Shut down the system

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Flush - Flushes the dry additive header with hot water. Can only be requested if already shutdown.

Open dry additive header water return valve XV2194

Open XV1312

Open XV1313

Start P-1310

Flush for 10 minutes

Shutdown

	Shutdown - Turns off the pump and all valves:

If Mix Conveyor C-1300 running,

Wait 20 seconds for conveyor to clear

Close Mix Tank Slide Gate G-1300

Stop P-1310

Stop A-1300

Set FIC1320 to manual, 0% output

Close XV1311

Close XV1312

Close XV1313

Close XV1314

Close XV1321

Close XV2152

Close XV2162

Close XV2194

	E-Shutdown - Immediately turns off the pump and all storage header valves:

Stop P-1310, A-1300

Set FIC1320 to manual, 0% output

Close XV1311, XV1312, XV1313, XV1314, XV1321, XV2152, XV2162, XV2194

### Dry Additive Makeup Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

C-1301 failure for 1 second  Shutdown

SS1301 indicates conveyor off 20 seconds after startup  Shutdown

Destination tank level > 90%   Shutdown

AS1302 indicates conveyor belt out of alignment for 3 seconds  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Wet Additive Makeup Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-1400 | Mix Tank agitator | Mix the additive into water |
| P-1410 | Mix Tank Unload Pump | Centrifugal pump that transfers liquid additive to wet additive header and to one of the additive ingredient storage tanks. |
| P-1440 | Wet Add Inlet Pump | Centrifugal pump that transfers liquid additive from stations to mix tank. |
| T-1400 | Additive Mix Tank | 500 gallon tank. Mixed additive is transferred from this tank. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI1400 | Indicator | pH of Mix Tank | Monitor pH to determine proper make-up | 0-14 |  |
| FI1440 | Indicator | Additive flow | Measures flow rate of additive pumped into mix tank | 0-50 gpm |  |
| FIC1422 | Loop | Hot water supply flow control | Controls feed rate of hot water to Mix tank | 0-50 gpm, Fail closed, direct acting |  |
| FQI1440 | Indicator | Totalized additive flow | Measures amount of additive placed into mix tank |  |  |
| FQI1422 | Indicator | Totalized hot water flow | Measures amount of hot water placed into mix tank |  |  |
| LI1400 | Indicator | Level of Mix Tank | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-1400 | Motor | Mix tank agitator | Mixes water and additive in mix tank |  |
| P-1410 | Pump | Mix Tank Unload Pump | Pumps liquid from mix tank into wet additive header |  |
| P-1410 | Pump | Wet Add Inlet Pump | Pumps liquid from one of the additive stations into mix tank |  |
| XV1411 | Valve | Mix Tank Outlet Valve | Allows flow of additive from mix tank into pump |  |
| XV1412 | Valve | Wet Mix Unload Valve | Allows flow of liquid from pump into wet mix header |  |
| XV1413 | Valve | Hot water clean supply valve | Allows flow of hot cleaning water into wet mix header |  |
| XV1414 | Valve | Drain Valve | Allows flow of liquid from pump to drain |  |
| XV1420 | Valve | Cold water supply Valve | Allows flow of cold water into mix tank |  |
| XV1421 | Valve | Hot water mixer supply valve | Allows flow of hot water into mixing tank |  |
| XV1441 | Valve | Additive station #1 outlet valve | Allows flow of additive at station #1 to pump |  |
| XV1442 | Valve | Additive station #2 outlet valve | Allows flow of additive at station #2 to pump |  |
| XV1443 | Valve | Additive station #3 outlet valve | Allows flow of additive at station #3 to pump |  |

Devices in Wet Ingredient Storage

| XV2151 | Valve | T-2150 Wet Add Feed Valve | Controls flow from wet additive header into T-2150 |  |
| --- | --- | --- | --- | --- |
| XV2161 | Valve | T-2160 Wet Add Feed Valve | Controls flow from wet additive header into T-2160 |  |
| XV2171 | Valve | T-2170 Wet Add Feed Valve | Controls flow from wet additive header into T-2170 |  |
| XV2192 | Valve | Wet Add Header Drain Valve | Controls flow from wet additive header to drain |  |

## Unit Operation Interactions

Dry Additive Makeup Unit Liquids unloaded from wet additive makeup must not go into the same destination tank being used by the dry additive makeup unit.

## Wet Additive Makeup Unit Operational States

Note: The operator must select a source station and a destination tank.

	Make-up - Makes up a new batch of additive from the hot water supply and one of the material addition stations, initiated by operator.

If LI1400, Mix Tank level >= 2%, abort.

Display prompt for operator and operator selects source and destination

If Dry Additive to selected destination tank is in operation, abort operation

Request amount of hot water and amount of additive from operator

###### Wait for confirmation from operator

Close all valves (one step)

Initialize FQI1422 and FQI1440

Put Hot Water Flow Controller FIC1422 in auto, setpoint = 40 gpm

Wait for amount of hot water, FQI1422

Start Agitator A-1400

Open appropriate XV144x valve

Start wet additive inlet pump P-1440

Wait for amount of additive, FQI1440

Stop wet additive inlet pump P-1440

Close appropriate XV144x valve

Open appropriate XV21x1

Open Wet Mix Unload Valve XV1412

Open Mix Tank Outlet Valve XV1411

Start pump P-1410

Wait for Mix Tank level to be less than 1% for 30 seconds

Shut down the system

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Flush - Flushes the dry additive header with hot water. Can only be requested if already shutdown.

Open wet additive header water return valve XV2192

Open XV1412

Open XV1413

Start P-1410

Flush for 10 minutes

Shutdown

	Shutdown - Turns off the pump and all valves:

Stop P-1410

Stop P-1440

Stop A-1400

Set FIC1422 to manual, 0% output

Close XV1411

Close XV1412

Close XV1413

Close XV1414

Close XV1420

Close XV1421

Close XV2151

Close XV2161

Close XV2192

	E-Shutdown - Immediately turns off the pump and all storage header valves:

Stop P-1410, P-1440, A-1400

Set FIC1422 to manual, 0% output

Close XV1411, XV1412, XV1413, XV1414, XV1420, XV1421, XV2151, XV2161, XV2192

### Wet Additive Makeup Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

Destination tank level > 90%   Shutdown

FI1440 < 1 gpm while transferring additive to tank for 2 seconds  Shutdown

SS1301 indicates conveyor off 20 seconds after startup  Shutdown

AS1302 indicates conveyor belt out of alignment for 3 seconds  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Wet Ingredient Storage Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| T-2110 | Ingred W Tank | 10,000 gallon storage tank to hold ingredient W. When needed, its contents are transferred to the blend unit. |
| T-2120 | Ingred X Tank | 10,000 gallon storage tank to hold ingredient W. When needed, its contents are transferred to the blend unit. |
| T-2130 | Ingred Y Tank | 10,000 gallon storage tank to hold ingredient Y. When needed, its contents are transferred to the blend unit. |
| T-2140 | Ingred Z Tank | 10,000 gallon storage tank to hold ingredient Z. When needed, its contents are transferred to the blend unit. |
| T-2150 | Ingred S Tank | 10,000 gallon storage tank. When needed, its contents are transferred to reactor 1. |
| T-2160 | Ingred T Tank | 10,000 gallon storage tank. When needed, its contents are transferred to reactor 2 or reactor 3. |
| T-2170 | Ingred U Tank | 10,000 gallon storage tank. When needed, its contents are transferred to reactor 4. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| LI2110 | Indicator | Level of Ingred. W | Monitor level | 0-100 (units %) |  |
| LI2120 | Indicator | Level of Ingred. X | Monitor level | 0-100 (units %) |  |
| LI2130 | Indicator | Level of Ingred. Y | Monitor level | 0-100 (units %) |  |
| LI2140 | Indicator | Level of Ingred. Z | Monitor level | 0-100 (units %) |  |
| LI2150 | Indicator | Level of Ingred. B in Storage Tank #1 | Monitor level | 0-100 (units %) |  |
| LI2160 | Indicator | Level of Ingred. B in Storage Tank #2 | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| XV2111 | Valve | T-2110 Truck Feed Valve | Controls flow from truck unload header into T-2110 |  |
| XV2112 | Valve | T-2110 Rail Feed Valve | Controls flow from rail unload header into T-2110 |  |
| XV2115 | Valve | T-2110 Discharge Valve | Controls flow from T-2110 to blend unit |  |
| XV2121 | Valve | T-2120 Truck Feed Valve | Controls flow from truck unload header into T-2120 |  |
| XV2122 | Valve | T-2120 Rail Feed Valve | Controls flow from rail unload header into T-2120 |  |
| XV2125 | Valve | T-2120 Discharge Valve | Controls flow from T-2120 to blend unit |  |
| XV2131 | Valve | T-2130 Truck Feed Valve | Controls flow from truck unload header into T-2130 |  |
| XV2132 | Valve | T-2130 Rail Feed Valve | Controls flow from rail unload header into T-2130 |  |
| XV2135 | Valve | T-2130 Discharge Valve | Controls flow from T-2130 to blend unit |  |
| XV2141 | Valve | T-2140 Truck Feed Valve | Controls flow from truck unload header into T-2140 |  |
| XV2142 | Valve | T-2140 Rail Feed Valve | Controls flow from rail unload header into T-2140 |  |
| XV2145 | Valve | T-2140 Discharge Valve | Controls flow from T-2140 to blend unit |  |
| XV2151 | Valve | T-2150 Wet Add Feed Valve | Controls flow from wet additive header into T-2150 |  |
| XV2152 | Valve | T-2150 Dry Add Feed Valve | Controls flow from dry additive header into T-2150 |  |
| XV2155 | Valve | T-2150 Discharge Valve | Controls flow from T-2150 to reactor 1 |  |
| XV2161 | Valve | T-2160 Wet Add Feed Valve | Controls flow from wet additive header into T-2160 |  |
| XV2162 | Valve | T-2160 Dry Add Feed Valve | Controls flow from dry additive header into T-2160 |  |
| XV2165 | Valve | T-2160 Discharge Valve | Controls flow from T-2160 to reactor 2 |  |
| XV2166 | Valve | T-2160 Discharge Valve | Controls flow from T-2160 to reactor 3 |  |
| XV2171 | Valve | T-2170 Wet Add Feed Valve | Controls flow from wet additive header into T-2170 |  |
| XV2175 | Valve | T-2170 Discharge Valve | Controls flow from T-2170 to reactor 4 |  |
| XV2192 | Valve | Wet Add Header Drain Valve | Controls flow from wet additive header to drain |  |
| XV2194 | Valve | Dry Add Header Drain Valve | Controls flow from dry additive header to drain |  |
| XV2196 | Valve | Truck Header Drain Valve | Controls flow from truck unload header to drain |  |
| XV2198 | Valve | Rail Header Drain Valve | Controls flow from rail unload header to drain |  |

## Unit Operation Interactions

Wet Unload Units Liquid ingredients are received from the truck wet unload unit and rail wet unload unit and transferred to the appropriate tank. The truck wet unload and rail wet unload units completely control the inlet side of the wet storage unit operation.

Additive Units Dry ingredients are received from the dry additive unit and liquid ingredients are received from the wet additive unit and transferred to the appropriate tank. The dry additive and wet additive units completely control the inlet side of the wet storage unit operation.

Blend Unit Liquid ingredients are transferred to the blend unit. The blend unit controls the outlet side of the appropriate tanks of the wet storage unit.

Reactor 1, Reactor 2, and Reactor 3 Units Liquid ingredients are transferred to the appropriate reactor unit. The reactor units control the outlet side of the appropriate tanks of the wet storage unit.

# Rail Dry Unload Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| B-1591 | Dust Collector Blower | Centrifugal fan that draws dust from conveyors to dust collector. |
| BE-1510 | Bucket Elevator Conveyor | Conveys dry ingredient to overhead conveyor |
| C-1503 | Left Rail Dump Conveyor | Conveys dry ingredient from left hopper to common conveyor, C-1505 |
| C-1504 | Right Rail Dump Conveyor | Conveys dry ingredient from right hopper to common conveyor, C-1505 |
| C-1505 | Rail Dump Conveyor | Conveys dry ingredient to bucket elevator |
| C-1520 | Overhead Conveyor 1 | Conveys dry ingredient from bucket elevator to conveyor 2. |
| C-1530 | Overhead Conveyor 2 | Conveys dry ingredient from conveyor 1 to dry ingredient storage. |
| G-1501 | Left Rail Dump Slide Gate | Dry ingredient enters system from left rail dump hopper. |
| G-1502 | Right Rail Dump Slide Gate | Dry ingredient enters system from right rail dump hopper. |
| T-1590 | Dust Collector | Holds dust drawn from conveyors. |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| AS1506 | AlignmentSwitch | C-1505 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| AS1521 | AlignmentSwitch | C-1520 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| AS1531 | AlignmentSwitch | C-1530 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| B-1591 | Motor | Dust Collector Vacuum Blower | Sucks dust from conveying system |  |
| BE-1510 | Bucket Elevator | Rail Dump Bucket Elevator | Moves dry ingredient from common rail dump conveyor to overhead conveyor |  |
| ES1523 | E-Stop Switch | C-1520 Belt E-Stop Pull Cord | Pull to e-stop conveyor |  |
| ES1533 | E-Stop Switch | C-1530 Belt E-Stop Pull Cord | Pull to e-stop conveyor |  |
| C-1503 | Conveyor | Left Rail Dump Conveyor | Moves dry ingredient from left rail dump hopper to common rail dump conveyor |  |
| C-1504 | Conveyor | Right Rail Dump Conveyor | Moves dry ingredient from right rail dump hopper to common rail dump conveyor |  |
| C-1505 | Conveyor | Common Rail Dump Conveyor | Moves dry ingredient from rail dump to bucket elevator |  |
| C-1520 | Conveyor | Overhead Conveyor 1 | Moves dry ingredient from bucket elevator to conveyor 2 |  |
| C-1530 | Conveyor | Overhead Conveyor 2 | Moves dry ingredient from conveyor 1 to dry ingredient storage |  |
| L-1592 | Motor | Dust Collector Air Lock | Discharges dust from dust collector |  |
| M-1501 | Motor | Left Slide Gate Motor | Allows dry ingredient from railcar to enter left rail dump conveyor |  |
| M-1502 | Motor | Right Slide Gate Motor | Allows dry ingredient from railcar to enter right rail dump conveyor |  |
| PS1508 | Plug Switch | C-1505 Belt Plug Switch | Indicates that grain plugging end of conveyor (off=plug) |  |
| PS1525 | Plug Switch | C-1520 Belt Plug Switch | Indicates that grain plugging end of conveyor (off=plug) |  |
| PS1535 | Plug Switch | C-1530 Belt Plug Switch | Indicates that grain plugging end of conveyor (off=plug) |  |
| SS1503 | Speed Switch | C-1503 Speed Switch | Indicates that left conveyor stopped |  |
| SS1504 | Speed Switch | C-1504 Speed Switch | Indicates that right conveyor stopped |  |
| SS1505 | Speed Switch | C-1505 Speed Switch | Indicates that conveyor stopped |  |
| SS1510 | Speed Switch | C-1510 Speed Switch | Indicates that conveyor stopped |  |
| SS1520 | Speed Switch | C-1520 Speed Switch | Indicates that conveyor stopped |  |
| SS1530 | Speed Switch | C-1530 Speed Switch | Indicates that conveyor stopped |  |
| ZSC1501 | Limit Switch | G-1501 slide gate switch | Indicates left slide gate closed |  |
| ZSO1501 | Limit Switch | G-1501 slide gate switch | Indicates left slide gate open |  |
| ZSC1502 | Limit Switch | G-1502 slide gate switch | Indicates right slide gate closed |  |
| ZSO1502 | Limit Switch | G-1502 slide gate switch | Indicates right slide gate open |  |

## Unit Operation Interactions

Dry Ingredient Storage Unit Dry ingredients unloaded from railcars are sent to the dry ingredient storage unit.

## Rail Dry Unload Unit Operational States

	Transfer – Starts transfer of the left or right railcar contents to desired destination tank. Steps:

Display prompt for operator and operator selects source and destination

If transfer to selected destination tank already in operation (presumably from truck dry unload unit), abort operation (jump to last step)

If destination tank is more than 80% full, abort operation (jump to last step)

Request Dry Storage to Start Path to proper destination tank

Wait for path started

Start B-1591

Start L-1592

Start C-1530

Start C-1520

Start BE-1510

Start C-1505

Start left or right rail dump conveyor

Open left or right rail slide gate

Wait until destination bin is full (level > 95%)

Shut down the system

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown – Orderly shutdown of conveyor system. If failure in upstream device, skip wait. For example, if failure in either C-1505, skip the succeeding 20 second delay). Steps skip wait:

Close both slide gates

Wait 10 seconds

Stop C-1503 and stop C-1504

Wait 20 seconds

Stop C-1505

Wait 20 seconds

Stop BE-1510

Stop L-1592

Wait 30 seconds

Stop C-1520

Wait 20 seconds

Stop C-1530

Stop B-1591

Request Dry Storage to Shutdown

Wait for Dry Storage to finish shutting down

	E-Shutdown - Immediately turns off all equipment:

Close both slide gates

Stop C-1503, C-1504, C-1505, BE-1510, C-1520, C1530

Stop L-1592, B-1591

### Rail Dry Ingredient Unload Unit Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

L-1592 failure for 1 second  Hold

B-1591 failure for 1 second  Hold

C-1503 failure for 1 second  Shutdown

C-1504 failure for 1 second  Shutdown

C-1505 failure for 1 second  Shutdown

BE-1510 failure for 1 second  Shutdown

C-1520 failure for 1 second  Shutdown

G-1501 failure for 1 second  Shutdown

G-1502 failure for 1 second  Shutdown

SS1503 indicates conveyor off 20 seconds after startup  Shutdown

SS1504 indicates conveyor off 20 seconds after startup  Shutdown

SS1505 indicates conveyor off 20 seconds after startup  Shutdown

SS1510 indicates bucket elevator off 20 seconds after startup  Shutdown

SS1520 indicates conveyor off 20 seconds after startup  Shutdown

SS1530 indicates conveyor off 20 seconds after startup  Shutdown

AS1506 indicates conveyor belt out of alignment for 3 seconds  E-Shutdown

AS1521 indicates conveyor belt out of alignment for 3 seconds  E-Shutdown

AS1531 indicates conveyor belt out of alignment for 3 seconds  E-Shutdown

PS1508 indicates conveyor plugged for 2 seconds  E-Shutdown

PS1525 indicates conveyor plugged for 2 seconds  E-Shutdown

PS1535 indicates conveyor plugged for 2 seconds  E-Shutdown

ES1523 indicates E-stop pull cord pulled for 1 second  E-Shutdown

ES1533 indicates E-stop pull cord pulled for 1 second  E-Shutdown

In transfer and Dry Storage not in requested path for 3 seconds  E-Shutdown

In transfer and lose heartbeat to Dry Storage for 10 seconds  E-Shutdown

Standard Aux, HOA, overload alarms on motors

Standard Fail to Open, Fail to Close alarms on slide gate

# Truck Dry Unload Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| B-1691 | Dust Collector Blower | Centrifugal fan that draws dust from conveyors to dust collector. |
| BE-1610 | Bucket Elevator Conveyor | Conveys dry ingredient to overhead conveyor |
| C-1604 | Live Bottom Hopper Conveyor | Conveys dry ingredient from hopper to conveyor, C-1605 |
| C-1607 | Truck Dump Conveyor | Conveys dry ingredient to bucket elevator |
| C-1620 | Overhead Conveyor 1 | Conveys dry ingredient from bucket elevator to conveyor 2. |
| C-1630 | Overhead Conveyor 2 | Conveys dry ingredient from conveyor 1 to dry ingredient storage. |
| P-1601 | Platform raiser hydraulic pump | Dry ingredient enters system from left rail dump hopper. |
| T-1690 | Dust Collector | Holds dust drawn from conveyors. |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| AS1605 | AlignmentSwitch | C-1604 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| AS1608 | AlignmentSwitch | C-1607 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| AS1621 | AlignmentSwitch | C-1620 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| AS1631 | AlignmentSwitch | C-1630 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| B-1691 | Motor | Dust Collector Vacuum Blower | Sucks dust from conveying system |  |
| BE-1610 | Bucket Elevator | Rail Dump Bucket Elevator | Moves dry ingredient from common rail dump conveyor to overhead conveyor |  |
| C-1607 | Conveyor | Truck Dump Conveyor | Moves dry ingredient from live bottom hopper to bucket elevator |  |
| C-1620 | Conveyor | Overhead Conveyor 1 | Moves dry ingredient from bucket elevator to conveyor 2 |  |
| C-1630 | Conveyor | Overhead Conveyor 2 | Moves dry ingredient from conveyor 1 to dry ingredient storage |  |
| ES1623 | E-Stop Switch | C-1620 Belt E-Stop Pull Cord | Pull to e-stop conveyor |  |
| ES1633 | E-Stop Switch | C-1630 Belt E-Stop Pull Cord | Pull to e-stop conveyor |  |
| L-1602 | Lift Control Up | Trailer Table Lift Cylinder Control | Causes hydraulic lift cylinder to raise trailer |  |
| L-1603 | Lift Control Down | Trailer Table Lift Cylinder Control | Causes hydraulic lift cylinder to lower trailer |  |
| L-1692 | Motor | Dust Collector Air Lock | Discharges dust from dust collector |  |
| P-1601 | Motor | Platform raiser hydraulic pump | Provides hydraulic pressure for cylinder to tilt trailer |  |
| PS1606 | Plug Switch | C-1604 Belt Plug Switch | Indicates that grain plugging end of conveyor (off=plug) |  |
| PS1609 | Plug Switch | C-1607 Belt Plug Switch | Indicates that grain plugging end of conveyor (off=plug) |  |
| PS1625 | Plug Switch | C-1620 Belt Plug Switch | Indicates that grain plugging end of conveyor (off=plug) |  |
| PS1635 | Plug Switch | C-1630 Belt Plug Switch | Indicates that grain plugging end of conveyor (off=plug) |  |
| SS1604 | Speed Switch | C-1604 Speed Switch | Indicates that live bottom conveyor stopped |  |
| SS1607 | Speed Switch | C-1607 Speed Switch | Indicates that conveyor stopped |  |
| SS1610 | Speed Switch | BE-1610 Speed Switch | Indicates that elevator stopped |  |
| SS1620 | Speed Switch | C-1620 Speed Switch | Indicates that conveyor stopped |  |
| SS1630 | Speed Switch | C-1630 Speed Switch | Indicates that conveyor stopped |  |
| ZSD1601 | Limit Switch | Dump lift cylinder switch | Indicates lift down |  |
| ZSU1601 | Limit Switch | Dump lift cylinder switch | Indicates lift up |  |

## Unit Operation Interactions

Dry Ingredient Storage Unit Dry ingredients unloaded from trucks are sent to the dry ingredient storage unit.

## Truck Dry Unload Unit Operational States

	Transfer – Starts transfer of the live bottom hopper contents to desired destination tank. Steps:

Display prompt for operator and operator selects destination

If transfer to selected destination tank already in operation (presumably from rail dry unload unit), abort operation (jump to last step)

If destination tank is more than 80% full, abort operation (jump to last step)

Request Dry Storage to Start Path to proper destination tank

Wait for path started

Start B-1691

Start L-1692

Start C-1630

Start C-1620

Start BE-1610

Start C-1607

Start C-1604

Start P-1601

Wait until destination bin is full (level > 95%)

Shut down the system

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown – Orderly shutdown of conveyor system. If failure in upstream device, skip wait. For example, if failure in C-1604, skip the succeeding 10 second delay). Steps:

Stop P-1601

Wait 10 seconds

Stop C-1604

Wait 10 seconds

Stop C-1607

Wait 20 seconds

Stop BE-1610

Stop L-1692

Wait 30 seconds

Stop C-1620

Wait 20 seconds

Stop C-1630

Stop B-1691

Request Dry Storage to Shutdown

Wait for Dry Storage to finish shutting down

	E-Shutdown - Immediately turns off all equipment:

Stop P-1601

Stop C-1604, C-1607, BE-1610, C-1620, C1630

Stop L-1692, B-1691

## Truck Dry Unload Manual Control

	Start/stop pump:

Panel pushbuttons

	Raise lift:

Activate L-1602 to raise lift

	Lower lift:

Activate L-1603 to lower lift

### Truck Dry Ingredient Unload Unit Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

L-1692 failure for 1 second  Hold

B-1691 failure for 1 second  Hold

C-1604 failure for 1 second  Shutdown

C-1607 failure for 1 second  Shutdown

BE-1610 failure for 1 second  Shutdown

C-1620 failure for 1 second  Shutdown

SS1604 indicates conveyor off 20 seconds after startup  Shutdown

SS1607 indicates conveyor off 20 seconds after startup  Shutdown

SS1610 indicates bucket elevator off 20 seconds after startup  Shutdown

SS1620 indicates conveyor off 20 seconds after startup  Shutdown

SS1630 indicates conveyor off 20 seconds after startup  Shutdown

AS1605 indicates conveyor belt out of alignment for 3 seconds  E-Shutdown

AS1608 indicates conveyor belt out of alignment for 3 seconds  E-Shutdown

AS1621 indicates conveyor belt out of alignment for 3 seconds  E-Shutdown

AS1631 indicates conveyor belt out of alignment for 3 seconds  E-Shutdown

PS1606 indicates conveyor plugged for 2 seconds  E-Shutdown

PS1609 indicates conveyor plugged for 2 seconds  E-Shutdown

PS1625 indicates conveyor plugged for 2 seconds  E-Shutdown

PS1635 indicates conveyor plugged for 2 seconds  E-Shutdown

ES1623 indicates E-stop pull cord pulled for 1 second  E-Shutdown

ES1633 indicates E-stop pull cord pulled for 1 second  E-Shutdown

In transfer and Dry Storage not in requested path for 3 seconds  E-Shutdown

In transfer and lose heartbeat to Dry Storage for 10 seconds  E-Shutdown

Standard Aux, HOA, overload alarms on motors

Standard Fail to Open, Fail to Close alarms on slide gate

# Dry Storage Loadin Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| C-2211 | First Storage Conveyor | Conveys dry ingredient from unload to Gate 1 |
| C-2231 | Second Storage Conveyor | Conveys dry ingredient from Gate 1 to Gate 2 |
| C-2251 | Third Storage Conveyor | Conveys dry ingredient from Gate 3 to T-2250 |
| G-2215 | Diverter Gate 1 | Conveys dry ingredient from first conveyor to T-2210 or second conveyor. |
| G-2235 | Diverter Gate 2 | Conveys dry ingredient from second conveyor to T-2230 or third conveyor. |
| T-2210 | Dry Ingredient Storage Tank 1 | Stores dry ingredient for use in reactor 2 |
| T-2230 | Dry Ingredient Storage Tank 2 | Stores dry ingredient for use in reactor 2 |
| T-2250 | Dry Ingredient Storage Tank 3 | Stores dry ingredient for use in reactor 2 |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| LI2210 | Indicator | Level of T-2210 | Monitor level | 0-100 (units %) |  |
| LI2230 | Indicator | Level of T-2230 | Monitor level | 0-100 (units %) |  |
| LI2250 | Indicator | Level of T-2250 | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| AS2212 | AlignmentSwitch | C-2211 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| AS2232 | AlignmentSwitch | C-2231 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| AS2252 | AlignmentSwitch | C-2251 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| C-2211 | Conveyor | First Storage Conveyor | Moves dry ingredient from unload unit to gate 1 |  |
| C-2231 | Conveyor | Second Storage Conveyor | Moves dry ingredient from gate 1 to gate 2 |  |
| C-2251 | Conveyor | Third Storage Conveyor | Moves dry ingredient from gate 2 to T-2250 |  |
| G-2215 | Gate Control | Gate 1 Solenoid Control | Changes gate 1 to divert to T-2210 or C-2231 |  |
| G-2235 | Gate Control | Gate 2 Solenoid Control | Changes gate 1 to divert to T-2230 or C-2251 |  |
| PS2215 | Plug Switch | C-2211 Belt Plug Switch | Indicates that grain plugging end of conveyor (off=plug) |  |
| PS2235 | Plug Switch | C-2231 Belt Plug Switch | Indicates that grain plugging end of conveyor (off=plug) |  |
| SS2211 | Speed Switch | C-2211 Speed Switch | Indicates that conveyor stopped |  |
| SS2231 | Speed Switch | C-2231 Speed Switch | Indicates that conveyor stopped |  |
| SS2251 | Speed Switch | C-2251 Speed Switch | Indicates that conveyor stopped |  |
| ZSL2215 | Limit Switch | G-2215 flop gate switch | Indicates flop gate in position to divert dry ingredient to T-2210 |  |
| ZSR2215 | Limit Switch | G-2215 flop gate switch | Indicates flop gate in position to divert dry ingredient to C-2231 |  |
| ZSL2235 | Limit Switch | G-2235 flop gate switch | Indicates flop gate in position to divert dry ingredient to T-2230 |  |
| ZSR2235 | Limit Switch | G-2235 flop gate switch | Indicates flop gate in position to divert dry ingredient to C-2251 |  |

## Unit Operation Interactions

Rail Dry Unload Unit Dry ingredients unloaded from railcars are conveyed to the dry ingredient storage unit. Rail Dry Unload controls the path startup and shutdown of Dry Storage Loadin.

Truck Dry Unload Unit Dry ingredients unloaded from trucks are conveyed to the dry ingredient storage unit. Truck Dry Unload controls the path startup and shutdown of Dry Storage Loadin.

## Dry Storage Loadin Unit Operational States

	Start Path to T-2210 – Starts equipment to transfer material from dry unload unit to T-2210. Do not allow this operation to start if any other load in path is in operation or if T-2210 is more than 95% full. Steps:

Put Gate 1 in position to transfer material to T-2210

Start C-2211

	Start Path to T-2230 – Starts equipment to transfer material from dry unload unit to T-2230. Do not allow this operation to start if any other load in path is in operation or if T-2230 is more than 95% full. Steps:

Put Gate 2 in position to transfer material to T-2230

Start C-2231

Put Gate 1 in position to transfer material to C-2231

Start C-2211

	Start Path to T-2250 – Starts equipment to transfer material from dry unload unit to T-2250. Do not allow this operation to start if any other load in path is in operation or if T-2250 is more than 95% full. Steps:

Start C-2251

Put Gate 2 in position to transfer material to C-2251

Start C-2231

Put Gate 1 in position to transfer material to C-2231

Start C-2211

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown – Orderly shutdown of conveyor system:

If C-2211 running,

Wait 30 seconds

Stop C-2211

If C-2231 running,

Wait 20 seconds

Stop C-2231

If C-2251 running,

Wait 20 seconds

Stop C-2251

	E-Shutdown - Immediately turns off all conveyors:

Stop C-2211, C-2231, C-2251

### Dry Storage Loadin Unit Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

C-2211 failure for 1 second  E-Shutdown

C-2231 failure for 1 second  E-Shutdown

C-2251 failure for 1 second  E-Shutdown

SS2211 indicates conveyor off 20 seconds after startup  E-Shutdown

SS2231 indicates conveyor off 20 seconds after startup  E-Shutdown

SS2251 indicates conveyor off 20 seconds after startup  E-Shutdown

AS2212 indicates conveyor belt out of alignment for 5 seconds  E-Shutdown

AS2232 indicates conveyor belt out of alignment for 5 seconds  E-Shutdown

AS2252 indicates conveyor belt out of alignment for 5 seconds  E-Shutdown

PS2215 indicates conveyor plugged for 2 seconds  E-Shutdown

PS2235 indicates conveyor plugged for 2 seconds  E-Shutdown

Standard Aux, HOA, overload alarms on motors

Standard Fail to Open, Fail to Close alarms on flop gates

Path active and shutdown complete of (either) dry storage unload  Shutdown

Path active and lose heartbeat to dry storage unload that commanded path  Shutdown

# Dry Storage Loadout Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| C-2290 | Outlet Conveyor | Conveys dry ingredient from storage tanks to reactor 2. |
| T-2210 | Dry Ingredient Storage Tank 1 | Stores dry ingredient for use in reactor 2 |
| T-2230 | Dry Ingredient Storage Tank 2 | Stores dry ingredient for use in reactor 2 |
| T-2250 | Dry Ingredient Storage Tank 3 | Stores dry ingredient for use in reactor 2 |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| AS2291 | AlignmentSwitch | C-2290 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| AS2292 | AlignmentSwitch | C-2290 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| C-2290 | Conveyor | Outlet Conveyor | Moves dry ingredient from bins to reactor 2 |  |
| L-2219 | Motor | T-2210 Air Lock | Discharges dry ingredient from T-2210 |  |
| L-2239 | Motor | T-2230 Air Lock | Discharges dry ingredient from T-2230 |  |
| L-2259 | Motor | T-2250 Air Lock | Discharges dry ingredient from T-2250 |  |
| SS2290 | Speed Switch | C-2290 Speed Switch | Indicates that conveyor stopped |  |

## Unit Operation Interactions

Reactor 2 Dry ingredients are conveyed to reactor 2 unit.

## Dry Storage Loadout Unit Operational States

	Start Path from T-2210 – Starts equipment to transfer material from T-2210 to reactor 2. Do not allow this operation to start if any other load out path is in operation or if T-2210 is less than 2% full. Steps:

Stop all airlocks (L-2219, L-2239, L-2259) – one step

Start C-2290

Start L-2219

	Start Path from T-2230 – Starts equipment to transfer material from T-2230 to reactor 2. Same as Start Path from T-2210, except use T-2230 and L-2239 in place of T-2210 and L-2219, respectively.

	Start Path from T-2250 – Starts equipment to transfer material from T-2250 to reactor 2. Same as Start Path from T-2210, except use T-2250 and L-2259 in place of T-2210 and L-2219, respectively.

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown – Orderly shutdown of conveyor system. If failure in conveyor, skip wait:

Stop L-2219

Stop L-2239

Stop L-2259

Wait 60 seconds

Stop C-2290

	E-Shutdown - Immediately turns off all devices:

Stop L-2219, L-2239, L-2259, C-2290

### Dry Storage Unit Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

L-2219 failure for 1 second  Loadout Shutdown

L-2239 failure for 1 second  Loadout Shutdown

L-2259 failure for 1 second  Loadout Shutdown

C-2290 failure for 1 second  Loadout E-Shutdown

SS2290 indicates conveyor off 20 seconds after startup  Loadout E-Shutdown

AS2291 indicates conveyor belt out of alignment for 5 seconds  Loadout E-Shutdown

AS2292 indicates conveyor belt out of alignment for 5 seconds  Loadout E-Shutdown

Standard Aux, HOA, overload alarms on motors

Shutdown of reactor using dry storage  Loadout Shutdown

Lose heartbeat with reactor using dry storage for 10 seconds  Loadout E-Shutdown

# Truck Powder Unload Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| T-2440 | Receiver/Air Filter | Holds powder drawn from truck before being conveyed to storage. Contains filter element that must be cleaned at intervals. |
| B-2445 | Truck Powder Unload Blower | Positive displacement blower to create vacuum and generate positive pressure conveying air flow. Transfers powder from one of two truck unload stations to truck unload header and to one of the powder ingredient storage tanks. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| FI2448 | Indicator | Truck unload header flow | Measure outflow of truck unload receiver | 0-300 lbs/min |  |
| FQI2448 | Indicator | Totalized truck unload transfer flow | Measure amount of ingredient transferred to tank |  |  |
| PI2442 | Indicator | Truck unload receiver tank pressure | Measure vacuum pressure of receiver tank | 0-15 psi vacuum |  |
| PI2443 | Indicator | XV2443 filter purge air pressure | Measure filter purge air pressure at truck unload receiver | 0-100 psi |  |
| PI2445 | Indicator | B-2445 suction | Measure blower suction pressure | 0-15 psi vacuum |  |
| PI2446 | Indicator | XV2447 air pressure | Measure air pressure at receiver outlet | 0-100 psi |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| B-2445 | Blower | Truck Powder Unload Blower | Transfers powder from truck stations into truck unload header |  |
| L-2441 | Motor | Receiver Air Lock | Discharges powder from receiver |  |
| XV2412 | Valve | Truck Station 1 Unload Valve | Allows flow of powder from truck station 1 into receiver |  |
| XV2422 | Valve | Truck Station 2 Unload Valve | Allows flow of powder from truck station 2 into receiver |  |
| XV2443 | Valve | Receiver Purge Inlet Valve | Allows flow of purge air into receiver for filter cleaning |  |
| XV2444 | Valve | Receiver Vent Valve | Allows air out of receiver during filter cleaning cycle |  |
| XV2447 | Valve | Truck Station Outlet Valve | Allows powder to flow from receiver to truck unload header | Must be open whenever blower is running. |

## Unit Operation Interactions

Rail Powder Unload Unit Powder unloaded from a truck trailer must not go into the same destination tank being used by the rail powder unload unit.

## Truck Powder Unload Unit Operational States

Note: The operator must select a source station and a destination tank.

	Transfer - Transfers the entire contents of the tank trailer at the selected truck unload station to the selected destination tank. Do not allow this operation to start if any Truck Transfer is in operation. Steps:

Display prompt for operator and operator selects source and destination

If destination tank is more than 80% full, abort operation (jump to last step)

If Rail Transfer to selected destination tank is in operation, abort operation

Close all valves (one step)

Initialize FQI2448

Open appropriate unload valve (XV2412 or XV2422)

Open XV2447

Open appropriate XV26x1

Start L-2441

Start B-2445

Wait until destination tank is full (level > 95%), or low flow in truck unload header (flow < 5 lbs/min)

Shut down the system

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Filter Clean – Cleans receiver filter with pressurized air. Can only be requested if already shutdown

Open XV2444

Open XV2443 for 0.5 sec

Pause 1 sec

Open XV2443 for 0.5 sec

Pause 1 sec

Open XV2443 for 0.5 sec

Pause 1 sec

Shut down the system

	Shutdown - Turns off the blower, air lock, and all valves:

Stop B-2445

Stop L-2441

Close XV2412

Close XV2422

Close XV2443

Close XV2444

Close XV2447

Close XV2611

Close XV2621

Close XV2631

Close XV2641

	E-Shutdown - Immediately turns off the blower, air lock, and all storage header valves:

Stop B-2445, Stop L-2441

Close XV2412, XV2422, XV2443, XV2444, XV2447, XV2611, XV2621, XV2631, XV2641

### Truck Powder Unload Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

PI2445 < 3 psi vacuum and B-2445 running for 20 seconds  Shutdown

PI2442 < 3 psi vacuum and B-2445 running for 30 seconds  Shutdown

PI2446 > 80 psi for 5 seconds  Alarm

PI2446 > 90 psi for 10 seconds  Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Rail Powder Unload Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| T-2490 | Receiver/Air Filter | Holds powder drawn from truck before being conveyed to storage. Contains filter element that must be cleaned at intervals. |
| B-2495 | Railcar Powder Unload Blower | Positive displacement blower to create vacuum and generate positive pressure conveying air flow. Transfers powder from one of two truck unload stations to truck unload header and to one of the powder ingredient storage tanks. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| FI2498 | Indicator | Railcar unload header flow | Measure outflow of railcar unload receiver | 0-300 lbs/min |  |
| FQI2498 | Indicator | Totalized railcar unload transfer flow | Measure amount of ingredient transferred to tank |  |  |
| PI2492 | Indicator | Railcar unload receiver tank pressure | Measure vacuum pressure of receiver tank | 0-15 psi vacuum |  |
| PI2493 | Indicator | XV2493 filter purge air pressure | Measure filter purge air pressure at railcar unload receiver | 0-100 psi |  |
| PI2495 | Indicator | B-2495 suction | Measure blower suction pressure | 0-15 psi vacuum |  |
| PI2496 | Indicator | XV2497 air pressure | Measure air pressure at receiver outlet | 0-100 psi |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| B-2495 | Blower | Railcar Powder Unload Blower | Transfers powder from railcar stations into rail unload header |  |
| L-2491 | Motor | Receiver Air Lock | Discharges powder from receiver |  |
| XV2452 | Valve | Railcar Station 1 Unload Valve | Allows flow of powder from railcar station 1 into receiver |  |
| XV2462 | Valve | Railcar Station 2 Unload Valve | Allows flow of powder from railcar station 2 into receiver |  |
| XV2493 | Valve | Receiver Purge Inlet Valve | Allows flow of purge air into receiver for filter cleaning |  |
| XV2494 | Valve | Receiver Vent Valve | Allows air out of receiver during filter cleaning cycle |  |
| XV2497 | Valve | Railcar Station Outlet Valve | Allows powder to flow from receiver to rail unload header | Must be open whenever blower is running. |

## Unit Operation Interactions

Truck Powder Unload Unit Powder unloaded from a railcar must not go into the same destination tank being used by the truck powder unload unit.

## Rail Powder Unload Unit Operational States

Note: The operator must select a source station and a destination tank.

	Transfer - Transfers the entire contents of the tank trailer at the selected railcar unload station to the selected destination tank. Do not allow this operation to start if any Rail Transfer is in operation. Steps:

Display prompt for operator and operator selects source and destination

If destination tank is more than 80% full, abort operation (jump to last step)

If Truck Transfer to selected destination tank is in operation, abort operation

Close all valves (one step)

Initialize FQI2498

Open appropriate unload valve (XV2452 or XV2462)

Open XV2497

Open appropriate XV26x2

Start L-2491

Start B-2495

Wait until destination tank is full (level > 95%), or low flow in rail unload header (flow < 5 lbs/min)

Shut down the system

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Filter Clean – Cleans receiver filter with pressurized air. Can only be requested if already shutdown

Open XV2494

Open XV2493 for 0.5 sec

Pause 1 sec

Open XV2493 for 0.5 sec

Pause 1 sec

Open XV2493 for 0.5 sec

Pause 1 sec

Shut down the system

	Shutdown - Turns off the blower, air lock, and all valves:

Stop B-2495

Stop L-2491

Close XV2452

Close XV2462

Close XV2493

Close XV2494

Close XV2497

Close XV2612

Close XV2622

Close XV2632

Close XV2642

	E-Shutdown - Immediately turns off the blower, air lock, and all storage header valves:

Stop B-2495, Stop L-2491

Close XV2452, XV2462, XV2493, XV2494, XV2497, XV2612, XV2622, XV2632, XV2642

### Rail Powder Unload Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

PI2495 < 3 psi vacuum and B-2495 running for 20 seconds  Shutdown

PI2492 < 3 psi vacuum and B-2495 running for 30 seconds  Shutdown

PI2496 > 80 psi for 5 seconds  Alarm

PI2496 > 90 psi for 10 seconds  Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Powder Ingredient Storage Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| B-2690 | Powder Convey Blower | Blower to generate positive pressure conveying air flow. Transfers powder from one of 4 storage tanks to reactor 3. |
| T-2610 | Ingred N Tank | 5,000 pound storage tank to hold ingredient N. When needed, its contents are transferred to reactor 3. |
| T-2620 | Ingred P Tank | 5,000 pound storage tank to hold ingredient P. When needed, its contents are transferred to reactor 3. |
| T-2630 | Ingred Q Tank | 5,000 pound storage tank to hold ingredient Q. When needed, its contents are transferred to reactor 3. |
| T-2640 | Ingred R Tank | 5,000 pound storage tank to hold ingredient R. When needed, its contents are transferred to reactor 3. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| LI2610 | Indicator | Level of Ingred. N | Monitor level | 0-100 (units %) |  |
| LI2620 | Indicator | Level of Ingred. P | Monitor level | 0-100 (units %) |  |
| LI2630 | Indicator | Level of Ingred. Q | Monitor level | 0-100 (units %) |  |
| LI2640 | Indicator | Level of Ingred. R | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| B-2690 | Blower | Powder Unload Blower | Transfers powder from storage tank to reactor 3 |  |
| L-2614 | Motor | T-2610 Outlet Air Lock | Discharges powder from T-2610 |  |
| L-2624 | Motor | T-2620 Outlet Air Lock | Discharges powder from T-2620 |  |
| L-2634 | Motor | T-2630 Outlet Air Lock | Discharges powder from T-2630 |  |
| L-2644 | Motor | T-2640 Outlet Air Lock | Discharges powder from T-2640 |  |
| XV2611 | Valve | T-2610 Truck Feed Valve | Controls flow from truck unload header into T-2610 |  |
| XV2612 | Valve | T-2610 Rail Feed Valve | Controls flow from rail unload header into T-2610 |  |
| XV2615 | Valve | T-2610 Discharge Valve | Controls flow from T-2610 to reactor 3 unit |  |
| XV2616 | Valve | T-2610 Pressurized Air Inlet | Controls flow into T-2610 to push powder out |  |
| XV2621 | Valve | T-2620 Truck Feed Valve | Controls flow from truck unload header into T-2620 |  |
| XV2622 | Valve | T-2620 Rail Feed Valve | Controls flow from rail unload header into T-2620 |  |
| XV2625 | Valve | T-2620 Discharge Valve | Controls flow from T-2620 reactor 3 unit |  |
| XV2626 | Valve | T-2620 Pressurized Air Inlet | Controls flow into T-2620 to push powder out |  |
| XV2631 | Valve | T-2630 Truck Feed Valve | Controls flow from truck unload header into T-2630 |  |
| XV2632 | Valve | T-2630 Rail Feed Valve | Controls flow from rail unload header into T-2630 |  |
| XV2635 | Valve | T-2630 Discharge Valve | Controls flow from T-2630 to reactor 3 unit |  |
| XV2636 | Valve | T-2630 Pressurized Air Inlet | Controls flow into T-2630 to push powder out |  |
| XV2641 | Valve | T-2640 Truck Feed Valve | Controls flow from truck unload header into T-2640 |  |
| XV2642 | Valve | T-2640 Rail Feed Valve | Controls flow from rail unload header into T-2640 |  |
| XV2645 | Valve | T-2640 Discharge Valve | Controls flow from T-2640 to reactor 3 unit |  |
| XV2646 | Valve | T-2640 Pressurized Air Inlet | Controls flow into T-2640 to push powder out |  |

## Unit Operation Interactions

Powder Unload Units Powder ingredients are received from the truck powder unload unit and rail powder unload unit and transferred to the appropriate tank. The truck powder unload and rail powder unload units completely control the inlet side of the powder storage unit operation.

Reactor 3 Unit Powder ingredients are transferred to this unit. The reactor 3 unit controls the blower and the outlet side of the appropriate tanks of the powder storage unit.

# Gas Storage Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| T-2810 | Gas A Storage Tank | 4,000 scf storage tank to hold gas ingredient A. When needed, its contents are transferred to reactor 4. |
| T-2820 | Gas B Storage Tank | 4,000 scf storage tank to hold gas ingredient B. When needed, its contents are transferred to reactor 4. |
| T-2830 | Gas C Storage Tank | 4,000 scf storage tank to hold gas ingredient C. When needed, its contents are transferred to reactor 4. |
| T-2840 | Gas D Storage Tank | 4,000 scf storage tank to hold gas ingredient D. When needed, its contents are transferred to reactor 4. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| PI2810 | Indicator | Pressure of Gas A | Monitor pressure | 0-500 psi |  |
| PI2820 | Indicator | Pressure of Gas B | Monitor pressure | 0-500 psi |  |
| PI2830 | Indicator | Pressure of Gas C | Monitor pressure | 0-500 psi |  |
| PI2840 | Indicator | Pressure of Gas D | Monitor pressure | 0-500 psi |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| XV2811 | Valve | T-2810 Feed Valve | Controls flow from gas ingredient unload into T-2810 |  |
| XV2815 | Valve | T-2810 Discharge Valve | Controls flow from T-2810 to reactor 4 unit |  |
| XV2821 | Valve | T-2820 Feed Valve | Controls flow from gas ingredient unload into T-2820 |  |
| XV2825 | Valve | T-2820 Discharge Valve | Controls flow from T-2820 reactor 4 unit |  |
| XV2831 | Valve | T-2830 Feed Valve | Controls flow from gas ingredient unload into T-2830 |  |
| XV2835 | Valve | T-2830 Discharge Valve | Controls flow from T-2830 to reactor 4 unit |  |
| XV2841 | Valve | T-2840 Feed Valve | Controls flow from gas ingredient unload into T-2840 |  |
| XV2645 | Valve | T-2840 Discharge Valve | Controls flow from T-2840 to reactor 4 unit |  |

## Unit Operation Interactions

Gas Unload Unit Gaseous ingredients are received from the gas unload unit and transferred to the appropriate tank. The gas unload unit completely controls the inlet side of the gas storage unit operation.

Reactor 4 Unit Gaseous ingredients are transferred to this unit. The reactor 4 unit controls the outlet side of the appropriate tanks of the gas storage unit.

# Blend Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| P-3001 | Raw W Outlet Pump | Centrifugal pump that transfers liquid product out of raw W storage tank to be blended and transported to one of two surge vessels. |
| P-3002 | Raw X Outlet Pump | Centrifugal pump that transfers liquid product out of raw X storage tank to be blended and transported to one of two surge vessels. |
| P-3003 | Raw Y Outlet Pump | Centrifugal pump that transfers liquid product out of raw Y storage tank to be blended and transported to one of two surge vessels. |
| P-3004 | Raw Z Outlet Pump | Centrifugal pump that transfers liquid product out of raw Z storage tank to be blended and transported to one of two surge vessels. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| FIC3001 | Loop | Raw W transfer flow control | Controls feed rate of raw W to surge vessel | 0-200 gpm, pump VS drive, cascade from surge level loop |  |
| FQI3001 | Indicator | Totalized raw W transfer flow | Measures amount of raw W transferred to surge |  |  |
| FIC3002 | Loop | Raw X transfer flow control | Controls feed rate of raw X to surge vessel | 0-200 gpm, pump VS drive, SP ratio of raw W flow rate level loop |  |
| FQI3002 | Indicator | Totalized raw X transfer flow | Measures amount of raw X transferred to surge |  |  |
| FIC3003 | Loop | Raw Y transfer flow control | Controls feed rate of raw Y to surge vessel | 0-200 gpm, pump VS drive, SP ratio of raw W flow rate level loop |  |
| FQI3003 | Indicator | Totalized raw Y transfer flow | Measures amount of raw Y transferred to surge |  |  |
| FIC3004 | Loop | Raw Z transfer flow control | Controls feed rate of raw Z to surge vessel | 0-200 gpm, pump VS drive, SP ratio of raw W flow rate level loop |  |
| FQI3004 | Indicator | Totalized raw Z transfer flow | Measures amount of raw Z transferred to surge |  |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| XV3001 | Valve | Raw W Feed Valve | Blocks flow of raw W into blend |  |
| XV3002 | Valve | Raw X Feed Valve | Blocks flow of raw X into blend |  |
| XV3003 | Valve | Raw Y Feed Valve | Blocks flow of raw Y into blend |  |
| XV3004 | Valve | Raw Z Feed Valve | Blocks flow of raw Z into blend |  |
| XV3011 | Valve | Blend to T-3001 outlet valve | Blocks flow of blend to reactor T-3001 |  |
| XV3013 | Valve | Blend to T-3002 outlet valve | Blocks flow of blend to reactor T-3002 |  |

Devices in Wet Ingredient Storage

| XV2115 | Valve | T-2110 Discharge Valve | Controls flow from T-2110 to blend unit |  |
| --- | --- | --- | --- | --- |
| XV2125 | Valve | T-2120 Discharge Valve | Controls flow from T-2120 to blend unit |  |
| XV2135 | Valve | T-2130 Discharge Valve | Controls flow from T-2130 to blend unit |  |
| XV2145 | Valve | T-2140 Discharge Valve | Controls flow from T-2140 to blend unit |  |

## Unit Operation Interactions

Wet Ingredient Storage Unit  Liquid ingredients are received from the wet ingredient storage unit. This unit has direct control over the outlet valves of selected tanks in the wet ingredient storage unit.

Reactor 1 Unit  Upon demand from the reactor 1 unit, liquid ingredient A is blended and transferred to the reactor unit.

Reactor 2 Unit  Upon demand from the reactor 2 unit, liquid ingredient A is blended and transferred to the reactor unit.

## Blend Unit Operational States

	Blend for Reactor 1 – Combines raw materials W, X, Y, and Z to produce ingredient A for reactor 1. Do not allow this operation if Blend for Reactor 1 or Blend for Reactor 2 is in operation. Steps:

Check all storage tank levels >= 20% and Reactor 1 in Make Batch

Close all valves (one step)

Operator verifies blend ratios okay

Reset all accumulators (FQI3001, FQI3002, FQI3003, FQI3004)

Open XV3011

Open XV3001

Open XV2115

If  FY3002 (X ratio) > 0.0

Open XV3002

Open XV2125

If  FY3003 (Y ratio) > 0.0

Open XV3003

Open XV2135

If  FY3004 (Z ratio) > 0.0

Open XV3004

Open XV2145

Start P-3001

Set Raw W Flow Controller FIC3001 to auto, setpoint = 200 gpm

If  FY3002 (X ratio) > 0.0

Start P-3002

Set FIC3002 to auto, setpoint from ratio of FT3001

If  FY3003 (Y ratio) > 0.0

Start P-3003

Set FIC3003 to auto, setpoint from ratio of FT3001

If  FY3004 (Z ratio) > 0.0

Start P-3004

Set FIC3004 to auto, setpoint from ratio of FT3001

Signal to Reactor 1 that all flows started

	Blend for Reactor 2 – Combines raw materials W, X, Y, and Z to produce ingredient A for reactor 2. Do not allow this operation if Blend for Reactor 1 or Blend for Reactor 2 is in operation. Steps:

Check all storage tank levels >= 20% and Reactor 2 in Make Batch

Close all valves (one step)

Operator verifies blend ratios okay

Reset all accumulators (FQI3001, FQI3002, FQI3003, FQI3004)

Open XV3013

Open XV3001

Open XV2115

If  FY3002 (X ratio) > 0.0

Open XV3002

Open XV2125

If  FY3003 (Y ratio) > 0.0

Open XV3003

Open XV2135

If  FY3004 (Z ratio) > 0.0

Open XV3004

Open XV2145

Start P-3001

Set Raw W Flow Controller FIC3001 to auto, setpoint = 200 gpm

If  FY3002 (X ratio) > 0.0

Start P-3002

Set FIC3002 to auto, setpoint from ratio of FI3001

If  FY3003 (Y ratio) > 0.0

Start P-3003

Set FIC3003 to auto, setpoint from ratio of FI3001

If  FY3004 (Z ratio) > 0.0

Start P-3004

Set FIC3004 to auto, setpoint from ratio of FI3001

Signal to Reactor T-3002 that all flows started

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Stop P-3001

Set FIC3001 to manual, 0% output

Close XV3001

Close XV2115

Stop P-3002

Set FIC3002 to manual, 0% output

Close XV3002

Close XV2125

Stop P-3003

Set FIC3003 to manual, 0% output

Close XV3003

Close XV2135

Stop P-3004

Set FIC3004 to manual, 0% output

Close XV3004

Close XV2145

Close XV3011

Close XV3013

	E-Shutdown - Immediately turns off all pumps and all valves:

Stop P-3001, P-3002, P-3003, P-3004

Set FIC3001 to manual, 0% output

Set FIC3002 to manual, 0% output

Set FIC3003 to manual, 0% output

Set FIC3004 to manual, 0% output

Close XV2115, XV2125, XV2135, XV2145

Close XV3001, XV3002, XV3003, XV3004, XV3011, XV3013

### Blend Unit Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI2110 < 5% for 20 seconds while blending to T-3001 or T-3002  Shutdown

LI2120 < 5% for 20 seconds and X ratio > 0.0  Shutdown

LI2130 < 5% for 20 seconds and Y ratio > 0.0  Shutdown

LI2140 < 5% for 20 seconds and Z ratio > 0.0  Shutdown

In Blend to Reactor 1 and Reactor 1 not in Make Batch  E-Shutdown

In Blend to Reactor 1 and lose heartbeat with Reactor 1 for 10 seconds  E-Shutdown

In Blend to Reactor 2 and Reactor 2 not in Make Batch  E-Shutdown

In Blend to Reactor 2 and lose heartbeat with Reactor 21 for 10 seconds  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

Lose heartbeat with reactor using blend for 10 seconds  E-Shutdown

# Reactor 1 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-3100 | Reactor Tank agitator | Mix the ingredients in the reactor tank to keep uniform |
| P-3100 | Reactor Outlet Pump | Centrifugal pump that transfers liquid product out of reactor to the ion exchange unit. |
| P-3102 | Ingredient S Pump | Centrifugal pump that transfers liquid ingredient S into the reactor tank. |
| T-3100 | Reactor Tank | 5,000 gallon tank to produce one batch of product. Ingredients are added and the reaction progresses to make product. When the analyzer indicates the batch is finished, it is transferred to the ion exchange unit. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI3100 | Indicator | pH of Product in Reactor Tank | Monitor pH | 0-14 |  |
| FI3101 | Indicator | Ingredient A flow rate | Monitor flow | 0-1000 gpm |  |
| FI3110 | Indicator | Rinse water flow rate | Monitor flow | 0-1000 gpm |  |
| FIC3102 | Loop | Ingredient S transfer flow control | Controls feed rate of ingredient S to reactor vessel | 0-600 gpm, Fail closed, direct acting |  |
| FQI3101 | Indicator | Totalized ingredient A transfer flow | Measures amount of ingredient A transferred to reactor |  |  |
| FQI3102 | Indicator | Totalized ingredient S transfer flow | Measures amount of ingredient S transferred to reactor |  |  |
| FQI3110 | Indicator | Totalized rinse water transfer flow | Measures amount of rinse water transferred to reactor |  |  |
| LI3100 | Indicator | Level of Reactor Tank | Monitor level | 0-100 (units %) |  |
| TI3100 | Indicator | Temperature of Reactor Tank | Monitor temperature | 70-140 deg F |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-3100 | Motor | Reactor tank agitator | Mixes ingredients in reactor tank | The agitator should not run when level falls below 2% |
| P-3100 | Motor | Reactor Outlet Pump | Pumps liquid product from reactor tank to ion exchange | This pump should not run if: LI3100<2% |
| P-3102 | Motor | Ingred. S Pump | Pumps ingredient S to reactor vessel | This pump should not run if PV:FIC3002<1.0 gpm and VO:FIC3002=100% |
| P-3110 | Motor | Rinse Water Return Pump | Pumps rinse water out of reactor vessel |  |
| XV2155 | Valve | Raw S Storage Discharge Valve | Controls flow of ingred. S out of tank |  |
| XV3100 | Valve | Reactor Discharge Valve | Controls flow of product out of reactor tank |  |
| XV3101 | Valve | Ingred. A Feed Valve | Blocks flow of ingred. A into reactor |  |
| XV3102 | Valve | Ingred. S Feed Valve | Blocks flow of ingred. S into reactor |  |
| XV3110 | Valve | Rinse Water Feed Valve | Blocks flow of rinse water into reactor |  |
| XV3111 | Valve | Rinse Water Discharge Valve | Controls flow of rinse water out of reactor |  |
| XV3121 | Valve | CIP to Reactor Valve | Controls flow of CIP water into piping to ion exchange |  |
| XV3122 | Valve | Product to Ion Exchange Xfer Valve | Controls flow of product to ion exchange |  |
| XV3123 | Valve | CIP Return Valve | Directs CIP water back to CIP System |  |

Devices in Wet Ingredient Storage

| XV2155 | Valve | T-2150 Discharge Valve – Ingred. S | Controls flow from T-2150 to reactor 1 |  |
| --- | --- | --- | --- | --- |

## Unit Operation Interactions

Wet Ingredient Storage Unit Ingredient S is received from the wet ingredient storage unit. This unit has direct control over one of the valves in the wet ingredient storage unit.

Blend A liquid ingredient is received from the blend unit. This unit commands the blend unit to transfer an ingredient mix.

QA Sample The QA sample unit is controlled by the reactor. When sampling is requested by the reactor unit, valve paths are set to direct reactor contents to the analyzer system and then returned to the reactor.

CIP System The reactor unit requests CIP water. When CIP is granted, CIP water is directed to the reactor discharge pump, and the outlet piping valves are properly set to transfer the remaining product in the piping to the ion exchanger and then return the cleaning water to the CIP tank. When the flush is finished, then the CIP system is requested to return to its normal online/recycle operation.

Ion Exchange Cell Liquid product is transferred to the ion exchange cell from the reactor. If neither ion exchange unit #1 or #2 is ready, no new batches will be made.

Water Unit Used to get rinse water to rinse reactor between batches.

## Reactor 1 Operational States

Note: the following steps assume fixed amounts of ingredients. Could be modified to use a recipe.

	Make Batch – Combines ingredient A and ingredient B to produce product. Do not allow this operation if Make Batch or Rinse or Flush is in operation. Steps:

Check Reactor Level LI3100 < 1% and TI3100 < 80 deg. F and either Ion Exchange online

Close all valves (one step)

Add 1000 gal. of water:

Reset FQI3110

Open XV3110

Wait for FQI3110 >= 1000 gal.

Close XV3110

Start A-3100

Add 1000 gal. of Ingredient A:

Reset FQI3101

Open XV3101

Request Blend Unit to Blend for Reactor 1 and wait for all blend flows started

Wait for FQI3101 >= 1000 gal.

Request Blend Unit to Shutdown and wait for Blend Unit Shutdown finished

Close XV3101

Agitate for 10 minutes

Add 3000 gal. of Ingredient S:

Reset FQI3102

Open XV2155

Open XV3102

Start P-3102

Set Ingred. S Flow Controller FIC3102 to auto, setpoint = 500 gpm

Wait for FQI3102 >= 3000 gal.

Stop P-3102

Set FIC3102 to manual, 0% output

Close XV3102

Agitate for 10 minutes

Request QA Sample from QA Sampling System

Wait for QA sample finished (display QA result to operator)

Prompt operator for additional agitation minutes

Agitate for additional minutes.

Request Lock Reactor 1 from QA Sample system

Wait for lock

Agitate for 2 minutes

Request Unlock Reactor1 from QA Sample system

Wait for unlock

If neither Ion Exchange online,

Request Ion Exchange #1 to startup and wait for Ion Exchange #1 starting

Wait for Ion Exchange #1 online

Open XV3122

Open XV3100

Start P-3100

Wait for reactor level LI3100 < 1%

Stop A-3100

Stop P-3100

Close XV3100

Close XV3122

Initiate Rinse

	Rinse – Rinse reactor vessel in preparation for next batch. Only allowed if reactor is at end of Make Batch or Shutdown. Steps:

Check Reactor Level LI3100 < 1%

Close all valves (one step)

Open XV3110

Wait for LI3100 >= 10%.

Start A-3100

Wait for LI3100 >= 95%.

Close XV3110

Agitate for 10 minutes

Open XV3111

Start P-3110

Wait for LI3100 <= 1%

Stop A-3100

Shutdown the system

	Flush - Flushes the piping to the ion exchange header with CIP water. Can only be requested if already shutdown

If neither Ion Exchange is Online,

Request Ion Exchange #1 to startup and wait for Ion Exchange #1 starting

Wait for Ion Exchange #1 online

If CIP System is in shutdown or e-shutdown,

Request CIP System to go online/recycle and wait for CIP system online

Request CIP System for Reactor 1 Path and wait for CIP system Reactor 1 path set

Open ion exchange feed valve XV3122

Open CIP to reactor feed valve XV3121

Start P-3100

Wait 3 minutes for product to be flushed into ion exchange. Then open XV3123 and close XV3122

Flush for 10 minutes

Request CIP system to go online/recycle and wait for XV6003 to be closed

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Stop A-3100

Stop P-3102

Stop P-3100

Stop P-3110

Close XV2155

Close XV3101

Close XV3102

Close XV3110

Close XV3100

Close XV3111

Close XV3121

Close XV3122

Close XV3123

	E-Shutdown - Immediately turns off all pumps and all valves:

Stop A-3100

Stop P-3100, P-3102, P-3110

Close XV2155, XV3101, XV3102, XV3110, XV3100, XV3111, XV3121, XV3122, XV3123

### Reactor 1 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI3100 > 96% for 20 seconds  Alarm

LI3100 > 98% for 20 seconds  Shut down process

LI3100 < 1% for 20 seconds while transferring product to ion exchange in progress  Shutdown

AI3100 < 6 or > 8 for 20 seconds while making batch  Alarm

AI3100 < 5.5 or > 8.5 for 20 seconds while making batch  Shutdown

TI3100 >= 110 deg F for 20 seconds while making batch  Alarm

TI3100 >= 125 deg F for 20 seconds while making batch  Shutdown

CIP_1 System not in Reactor 1 Path when Reactor in steps where CIP_1 system used  E-Shutdown

Lose heartbeat with CIP_1 System for 10 seconds when Reactor in steps where CIP_1 system used  Hold

Adding Ingredient S and T2150 level < 2%  Shutdown

QA System not in Lock R1 in steps waiting for valid QA sample reading after QA System confirmed in Lock R1 state  Shutdown

Lose heartbeat with QA System for 10 seconds when in steps using the QA system  Hold

Ion Exchange #1 or Ion Exchange #2 not online when transferring product from reactor  Hold

Lose heartbeat with Ion Exchange #1 for 10 seconds and lose heartbeat with Ion Exchange #2 for 10 seconds  Hold

Blend shutdown when adding ingredient A   Hold

Lose heartbeat with Blend for 10 seconds when adding ingredient A   Hold

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Reactor 2 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-3200 | Reactor Tank agitator | Mix the ingredients in the reactor tank to keep uniform |
| P-3200 | Reactor Outlet Pump | Centrifugal pump that transfers liquid product out of reactor to the ion exchange unit. |
| C-3250 | Ingredient C Conveyor | Transfers dry ingredient C into the reactor tank. |
| T-3200 | Reactor Tank | 5,000 gallon tank to produce one batch of product. Ingredients are added and the reaction progresses to make product. When the analyzer indicates the batch is finished, it is transferred to the ion exchange unit. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI3200 | Indicator | pH of Product in Reactor Tank | Monitor pH | 0-14 |  |
| FI3201 | Indicator | Ingredient A flow rate | Monitor flow | 0-1000 gpm |  |
| FI3210 | Indicator | Rinse water flow rate | Monitor flow | 0-1000 gpm |  |
| FI3250 | Indicator | Ingredient A flow rate | Monitor flow | 0-500 lbs/min. |  |
| FIC3210 | Loop | Rinse water flow control | Controls flow rate of rinse water into reactor vessel | 0-1000 gpm, Fail closing, direct acting |  |
| FQI3201 | Indicator | Totalized ingredient A transfer flow | Measures amount of ingredient A transferred to reactor |  |  |
| FQI3210 | Indicator | Totalized rinse water transfer flow | Measures amount of rinse water transferred to reactor |  |  |
| FQI3250 | Indicator | Totalized dry ingredient transfer flow | Measures amount of dry ingredient transferred to reactor |  |  |
| LI3200 | Indicator | Level of Reactor Tank | Monitor level | 0-100 (units %) |  |
| TI3200 | Indicator | Temperature of Reactor Tank | Monitor temperature | 70-140 deg F |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-3200 | Motor | Reactor tank agitator | Mixes ingredients in reactor tank | The agitator should not run when level falls below 2% |
| AS3251 | AlignmentSwitch | C-3250 Belt Alignment Switch | Indicates that conveyor belt out of alignment (off=misalign) |  |
| C-3250 | Conveyor | Ingred. C Feed Conveyor | Feeds ingred. C into reactor |  |
| P-3200 | Motor | Reactor Outlet Pump | Pumps liquid product from reactor tank to ion exchange | This pump should not run if: LI3200<0.5% and not in flush |
| P-3210 | Motor | Rinse Water Return Pump | Pumps rinse water out of reactor vessel |  |
| SS3250 | Speed Switch | C-3250 Speed Switch | Indicates that conveyor stopped |  |
| XV3200 | Valve | Reactor Discharge Valve | Controls flow of product out of reactor tank |  |
| XV3201 | Valve | Ingred. A Feed Valve | Blocks flow of ingred. A into reactor |  |
| XV3210 | Valve | Rinse Water Feed Valve | Blocks flow of rinse water into reactor |  |
| XV3211 | Valve | Rinse Water Discharge Valve | Controls flow of rinse water out of reactor |  |
| XV3221 | Valve | CIP to Reactor Valve | Controls flow of CIP water into piping to ion exchange |  |
| XV3222 | Valve | Product to Ion Exchange Xfer Valve | Controls flow of product to ion exchange |  |
| XV3223 | Valve | CIP Return Valve | Directs CIP water back to CIP System |  |

Devices in Wet Ingredient Storage

| XV2165 | Valve | T-2160 Discharge Valve – Ingred. T | Controls flow from T-2160 to reactor 2 |  |
| --- | --- | --- | --- | --- |

## Unit Operation Interactions

Blend A liquid ingredient is received from the blend unit. This unit commands the blend unit to transfer an ingredient mix.

Dry Ingredient Storage Unit Dry ingredients are received from the dry ingredient storage unit. This unit has control over the dry ingredient storage unit.

QA Sample The QA sample unit is controlled by the reactor. When sampling is requested by the reactor unit, valve paths are set to direct reactor contents to the analyzer system and then returned to the reactor.

CIP System The reactor unit requests CIP water. When CIP is granted, CIP water is directed to the reactor discharge pump, and the outlet piping valves are properly set to transfer the remaining product in the piping to the ion exchanger and then return the cleaning water to the CIP tank. When the flush is finished, then the CIP system is requested to return to its normal online/recycle operation.

Ion Exchange Cell Liquid product is transferred to the ion exchange cell from the reactor. If neither ion exchange unit is ready, no new batches will be made.

Rinse Water Unit Used to get rinse water to rinse reactor between batches.

## Reactor 2 Operational States

	Make Batch – Combines ingredient A and ingredient B to produce product. Do not allow this operation if Make Batch or Rinse or Flush is in operation. Steps:

Check Reactor Level LI3200 < 1% and TI3200 < 80 deg. F and either Ion Exchange online

Display prompt for operator and operator selects dry ingredient source

Close all valves (one step)

Add 1000 gal. of water:

Reset FQI3210

Open XV3210

Set Water Flow Controller FIC3210 to auto, setpoint = 100 gpm

Wait for FQI3210 >= 1000 gal.

Set FIC3210 to manual, 0% output

Close XV3210

Start A-3200

Add 1000 gal. of Ingredient A:

Reset FQI3201

Open XV3201

Request Blend Unit to Blend for T-3201

Wait for all blend flows started

Wait for FQI3201 >= 1000 gal.

Request Blend Unit to Shutdown

Wait for Blend Unit Shutdown finished

Close XV3201

Agitate for 5 minutes

Add Ingredient C:

Reset FQI3250

Start C-3250

Start path from selected dry storage tank

Wait for path set

Wait for FQI3250 >= 500 lbs.

Start Dry Storage Loadout Shutdown

Wait for Dry Storage Loadout Shutdown complete

Wait 20 seconds

Stop C-3250

Agitate for 10 minutes

Request QA Sample from QA Sampling System

Wait for QA sample finished

Display QA result to operator

Prompt operator for additional agitation minutes

Agitate for additional minutes.

Request Lock Reactor 2 from QA Sample system

Wait for lock

Agitate for 2 minutes

Request Unlock Reactor 2 from QA Sample system

Wait for unlock

If neither Ion Exchange online,

Request Ion Exchange #2 to startup and wait for Ion Exchange #2 starting

Wait for Ion Exchange #2 online

Open XV3222

Open XV3200

Start P-3200

Wait for reactor level LI3200 < 1%

Stop A-3200

Stop P-3200

Close XV3200

Close XV3222

Initiate Rinse

	Rinse – Rinse reactor vessel in preparation for next batch. Only allowed if reactor is at end of Make Batch or Shutdown. Steps:

Check Reactor Level LI3200 < 1%

Close all valves (one step)

Open XV3210

Set Water Flow Controller FIC3210 to manual, 100% output

Wait for LI3200 >= 10%.

Start A-3200

Wait for LI3200 >= 95%.

Set FIC3210 to manual, 0% output

Close XV3210

Agitate for 10 minutes

Open XV3211

Start P-3210

Wait for LI3200 <= 1%

Stop A-3200

Shutdown the system

	Flush - Flushes the piping to the ion exchange header with CIP water. Can only be requested if already shutdown

If neither Ion Exchange online,

Request Ion Exchange #2 to startup and wait for Ion Exchange #2 starting

Wait for Ion Exchange #2 online

If CIP System is in shutdown or e-shutdown,

Request CIP System to go online/recycle

Wait for CIP system online

Request CIP System for Reactor 2 Path

Wait for CIP system Reactor 2 path set

Open ion exchange feed valve XV3222

Open CIP to reactor feed valve XV3221

Start P-3200

Wait 3 minutes for product to be flushed into ion exchange. Then open XV3223 and close XV3222

Flush for 10 minutes

Request CIP system to go online/recycle and wait for XV6006 to be closed

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Stop A-3200

Stop P-3200

Stop P-3210

Stop C-3250

Close XV3201

Set FIC3210 to manual, 0% output

Close XV3210

Close XV3200

Close XV3211

Close XV3221

Close XV3222

Close XV3223

	E-Shutdown - Immediately turns off all pumps and all valves:

Stop A-3200

Stop P-3200, P-3210, C-3250

Set FIC3210 to manual, 0% output

Close XV3201, XV3210, XV3200, XV3211, XV3221, XV3222, XV3223

### Reactor 2 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI3200 > 96% for 20 seconds  Alarm

LI3200 > 98% for 20 seconds  Shut down process

LI3200 < 1% for 20 seconds while transferring product to ion exchange in progress  Shutdown

AI3200 < 6 or > 8 for 20 seconds while making batch  Alarm

AI3200 < 5.5 or > 8.5 for 20 seconds while making batch  Shutdown

TI3200 >= 110 deg F for 20 seconds while making batch  Alarm

TI3200 >= 125 deg F for 20 seconds while making batch  Shutdown

SS3250 indicates conveyor off 20 seconds after startup  E-Shutdown

AS3251 indicates conveyor belt out of alignment for 5 seconds  E-Shutdown

CIP_1 System not in Reactor 2 Path when Reactor in steps where CIP_1 system used  E-Shutdown

Lose heartbeat with CIP_1 System for 10 seconds when Reactor in steps where CIP_1 system used  Hold

QA System not in Lock R2 in steps waiting for valid QA sample reading after QA System confirmed in Lock R2 state  Shutdown

Lose heartbeat with QA System for 10 seconds when in steps using the QA system  Hold

Ion Exchange #1 and Ion Exchange #2 not online when transferring product from reactor   Hold

Lose heartbeat with Ion Exchange #1 for 10 seconds and lose heartbeat with Ion Exchange #2 for 10 seconds  Hold

Blend shutdown when adding ingredient A   Hold

Lose heartbeat with Blend for 10 seconds when adding ingredient A   Hold

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Reactor 3 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-3300 | Reactor Tank agitator | Mix the ingredients in the reactor tank to keep uniform |
| P-3300 | Reactor Outlet Pump | Centrifugal pump that transfers liquid product out of reactor to the ion exchange unit. |
| P-3302 | Ingredient T Pump | Transfers wet ingredient T into the reactor tank. |
| T-3300 | Reactor Tank | 3,000 gallon tank to produce one batch of product. Ingredients are added and the reaction progresses to make product. When the analyzer indicates the batch is finished, it is transferred to the ion exchange unit. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI3300 | Indicator | pH of Product in Reactor Tank | Monitor pH | 0-14 |  |
| FI3301 | Indicator | Powder ingredient flow rate | Monitor flow | 0-200 lbs/min |  |
| FI3302 | Indicator | Ingred. T flow rate | Monitor flow | 0-300 gpm |  |
| FI3330 | Indicator | Rinse water flow rate | Monitor flow | 0-500 gpm |  |
| FIC3302 | Loop | Ingred. T flow rate controller | Control flow of ingred. T into reactor | 0-300 gpm |  |
| FIC3310 | Loop | Water flow rate controller | Control flow of water into reactor | 0-500 gpm |  |
| FQI3301 | Indicator | Totalized powder ingredient transfer flow | Measures amount of powder ingredient transferred to reactor |  |  |
| FQI3302 | Indicator | Totalized ingred. T transfer flow | Measures amount of ingredient T transferred to reactor |  |  |
| FQI3310 | Indicator | Totalized rinse water transfer flow | Measures amount of rinse water transferred to reactor |  |  |
| LI3300 | Indicator | Level of Reactor Tank | Monitor level | 0-100 (units %) |  |
| TI3300 | Indicator | Temperature of Reactor Tank | Monitor temperature | 70-140 deg F |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-3300 | Motor | Reactor tank agitator | Mixes ingredients in reactor tank | The agitator should not run when level falls below 2% |
| P-3300 | Motor | Reactor Outlet Pump | Pumps liquid product from reactor tank to ion exchange | This pump should not run if: LI3300<2% |
| P-3302 | Motor | Ingredient T Pump | Pumps ingredient T into reactor vessel |  |
| P-3310 | Motor | Rinse Water Return Pump | Pumps rinse water out of reactor vessel |  |
| XV3300 | Valve | Reactor Discharge Valve | Controls flow of product out of reactor tank |  |
| XV3301 | Valve | Powder Ingred. Feed Valve | Blocks flow of powder ingred. into reactor |  |
| XV3302 | Valve | Ingred. T Feed Valve | Blocks flow of ingred. T into reactor |  |
| XV3310 | Valve | Rinse Water Feed Valve | Blocks flow of rinse water into reactor |  |
| XV3311 | Valve | Rinse Water Discharge Valve | Controls flow of rinse water out of reactor |  |
| XV3321 | Valve | Rinse to Piping Valve | Controls flow of rinse water into piping to ion exchange |  |
| XV3322 | Valve | Product to Ion Exchange Xfer Valve | Controls flow of product to ion exchange |  |
| XV3323 | Valve | Rinse Water Return Valve at Ion Exchg | Directs Rinse water back to drain |  |

Devices in Wet Ingredient Storage

| XV2166 | Valve | T-2160 Discharge Valve – Ingred. T | Controls flow from T-2160 to reactor 3 |  |
| --- | --- | --- | --- | --- |

Devices in Powder Ingredient Storage

| B-2690 | Blower | Powder Unload Blower | Transfers powder from storage tank to reactor 3 |  |
| --- | --- | --- | --- | --- |
| L-2614 | Motor | T-2610 Outlet Air Lock | Discharges powder from T-2610 |  |
| L-2624 | Motor | T-2620 Outlet Air Lock | Discharges powder from T-2620 |  |
| L-2634 | Motor | T-2630 Outlet Air Lock | Discharges powder from T-2630 |  |
| L-2644 | Motor | T-2640 Outlet Air Lock | Discharges powder from T-2640 |  |
| XV2615 | Valve | T-2610 Discharge Valve | Controls flow from T-2610 to reactor 3 |  |
| XV2625 | Valve | T-2620 Discharge Valve | Controls flow from T-2620 to reactor 3 |  |
| XV2635 | Valve | T-2630 Discharge Valve | Controls flow from T-2630 to reactor 3 |  |
| XV2645 | Valve | T-2640 Discharge Valve | Controls flow from T-2640 to reactor 3 |  |
| XV2616 | Valve | T-2610 Pressure Air Inlet Valve | Air to help blow powder from T-2610 to reactor 3 |  |
| XV2626 | Valve | T-2620 Pressure Air Inlet Valve | Air to help blow powder from T-2620 to reactor 3 |  |
| XV2636 | Valve | T-2630 Pressure Air Inlet Valve | Air to help blow powder from T-2630 to reactor 3 |  |
| XV2646 | Valve | T-2640 Pressure Air Inlet Valve | Air to help blow powder from T-2640 to reactor 3 |  |

## Unit Operation Interactions

Powder Storage Unit Powder ingredients are received from the powder storage unit. This unit has direct control over the outlet side of the storage tanks in the powder storage unit.

Wet Ingredient Storage Unit Ingredient T is received from the wet ingredient storage unit. This unit has direct control over one of the valves in the wet ingredient storage unit.

Ion Exchange Cell Liquid product is transferred to the ion exchange cell from the reactor. If neither ion exchange 3 or 4 unit is ready, no new batches will be made.

Rinse Water Unit Used to get rinse water to rinse reactor between batches.

## Reactor 3 Operational States

	Make Batch – Combines powder and ingredient T to produce product. Do not allow this operation if Make Batch or Rinse or Flush is in operation. Steps:

Check Reactor Level LI3300 < 1% and TI3300 < 80 deg. F and either Ion Exchange 3 or 4 online

Display prompt for operator and operator selects powder source

Close all valves (one step)

Add 2000 gal. of water:

Reset FQI3310

Open XV3310

Set Water Flow Controller FIC3310 to auto, setpoint = 250 gpm

Wait for FQI3310 >= 2000 gal.

Set FIC3310 to manual, 0% output

Close XV3310

Start A-3300

Add 450 lbs. of powder:

Reset FQI3301

Open XV3301

Open appropriate powder tank outlet valve (XV26x5)

Start appropriate powder tank airlock valve motor (L-26x4)

Open appropriate powder tank pressurized air inlet valve (XV26x6)

Start B-2690

Wait for FQI3301 >= 450 lbs.

Close all XV26x6 (one step)

Stop all L-26x4 (one step)

Wait for FI3301 < 5 lbs/min

Stop B-2690

Close XV3301

Agitate for 5 minutes

Add Ingredient T:

Reset FQI3302

Open XV3302

Open XV2166

Set Ingred T Flow Controller FIC3302 to auto, setpoint = 200 gpm

Start P-3302

Wait for FQI3302 >= 500 gal.

Stop P-3302

Set FIC3302 to manual, 0% output

Agitate for 10 minutes

[Operator takes sample from reactor]

Prompt operator for additional agitation minutes

Agitate for additional minutes.

If neither Ion Exchange 3 or 4 is Online,

Request Ion Exchange #3 to startup and wait for Ion Exchange #3 starting

Wait for Ion Exchange #3 online

Open XV3322

Open XV3300

Start P-3300

Wait for reactor level LI3300 < 1%

Stop A-3300

Stop P-3300

Close XV3300

Close XV3322

Initiate Rinse

	Rinse – Rinse reactor vessel in preparation for next batch. Only allowed if reactor is at end of Make Batch or Shutdown. Steps:

Check Reactor Level LI3300 < 1%

Close all valves (one step)

Open XV3310

Set Water Flow Controller FIC3310 to manual, 100% output

Wait for LI3300 >= 10%.

Start A-3300

Wait for LI3300 >= 95%.

Set FIC3310 to manual, 0% output

Close XV3310

Agitate for 10 minutes

Open XV3311

Start P-3310

Wait for LI3300 <= 1%

Stop A-3300

Shutdown the system

	Flush - Flushes the piping to the ion exchange header with rinse water. Can only be requested if already shutdown

If neither Ion Exchange 3 or 4 is Online,

Request Ion Exchange #3 to startup and wait for Ion Exchange #3 starting

Wait for Ion Exchange #3 online

Open ion exchange feed valve XV3322

Open Rinse water to piping feed valve XV3321

Start P-3300

Wait 3 minutes for product to be flushed into ion exchange. Then open XV3323 and close XV3322

Flush for 10 minutes

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Stop B-2690

Stop all L26x4 (one step)

Close all XV26x6 (one step)

Close all XV26x5 (one step)

Close XV3301

Stop A-3300

Close XV2166

Stop P-3302

Stop P-3300

Stop P-3310

Set FIC3302 to manual, 0% output

Close XV3302

Set FIC3310 to manual, 0% output

Close XV3310

Close XV3300

Close XV3311

Close XV3321

Close XV3322

Close XV3323

	E-Shutdown - Immediately turns off all pumps and all valves:

Stop B-2690, L26x4

Close all XV26x6, XV26x5

Stop A-3300

Stop P-3300, P-3302, P-3310

Set FIC3302 to manual, 0% output

Set FIC3310 to manual, 0% output

Close XV2166, XV3301, XV3302, XV3310, XV3300, XV3311, XV3321, XV3322, XV3323

### Reactor 3 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI3300 > 96% for 20 seconds  Alarm

LI3300 > 98% for 20 seconds  Shut down process

LI3300 < 1% for 20 seconds while transferring product to ion exchange in progress  Shutdown

AI3300 < 6 or > 8 for 20 seconds while making batch  Alarm

AI3300 < 5.5 or > 8.5 for 20 seconds while making batch  Shutdown

TI3300 >= 110 deg F for 20 seconds while making batch  Alarm

TI3300 >= 125 deg F for 20 seconds while making batch  Shutdown

Ion Exchange #3 or Ion Exchange #4 is not online when transferring product to ion exchange  E-Shutdown

Lose heartbeat with Ion Exchange #3 for 10 seconds and lose heartbeat with Ion Exchange #4 for 10 seconds  Hold

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Reactor 4 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-3400 | Reactor Tank agitator | Mix the ingredients in the reactor tank to keep uniform |
| P-3400 | Reactor Outlet Pump | Centrifugal pump that transfers liquid product out of reactor to the ion exchange unit. |
| C-3402 | Ingredient U Pump | Transfers wet ingredient U into the reactor tank. |
| T-3400 | Reactor Tank | 2,000 gallon tank to produce one batch of product. Ingredients are added and the reaction progresses to make product. When the batch is finished, it is transferred to the ion exchange unit. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI3400 | Indicator | pH of Product in Reactor Tank | Monitor pH | 0-14 |  |
| FI3401 | Indicator | Powder ingredient flow rate | Monitor flow | 0-200 lbs/min |  |
| FI3402 | Indicator | Ingred. T flow rate | Monitor flow | 0-300 gpm |  |
| FI3411 | Indicator | Rinse water flow rate | Monitor flow | 0-500 gpm |  |
| FI3412 | Indicator | CIP fluid flow rate | Monitor flow | 0-500 gpm |  |
| FQI3401 | Indicator | Totalized powder ingredient transfer flow | Measures amount of powder ingredient transferred to reactor |  |  |
| FQI3402 | Indicator | Totalized ingred. T transfer flow | Measures amount of ingredient T transferred to reactor |  |  |
| FQI3411 | Indicator | Totalized rinse water transfer flow | Measures amount of rinse water transferred to reactor |  |  |
| FQI3412 | Indicator | Totalized CIP fluid transfer flow | Measures amount of CIP fluid transferred to reactor |  |  |
| LI3400 | Indicator | Level of Reactor Tank | Monitor level | 0-100 (units %) |  |
| TI3400 | Indicator | Temperature of Reactor Tank | Monitor temperature | 70-140 deg F |  |

Devices in Gas Storage

| XV2815 | Valve | T-2810 Discharge Valve | Controls flow from T-2810 to reactor 4 |  |
| --- | --- | --- | --- | --- |
| XV2825 | Valve | T-2820 Discharge Valve | Controls flow from T-2820 to reactor 4 |  |
| XV2835 | Valve | T-2830 Discharge Valve | Controls flow from T-2830 to reactor 4 |  |
| XV2845 | Valve | T-2840 Discharge Valve | Controls flow from T-2840 to reactor 4 |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-3400 | Motor | Reactor tank agitator | Mixes ingredients in reactor tank | The agitator should not run when level falls below 2% |
| P-3400 | Motor | Reactor Outlet Pump | Pumps liquid product from reactor tank to ion exchange | This pump should not run if: LI3400<1% |
| P-3402 | Motor | Ingredient U Pump | Pumps ingredient U into reactor vessel |  |
| XV3400 | Valve | Reactor Discharge Valve | Controls flow of product out of reactor tank |  |
| XV3401 | Valve | Gas Ingredient Feed Valve | Blocks flow of gas ingred. into reactor |  |
| XV3402 | Valve | Ingred. U Feed Valve | Blocks flow of ingred. U into reactor |  |
| XV3411 | Valve | Water Feed Valve | Blocks flow of water into reactor |  |
| XV3412 | Valve | CIP Fluid Feed Valve | Blocks flow of CIP fluid into reactor |  |
| XV3422 | Valve | Product to Ion Exchange Xfer Valve | Controls flow of product to ion exchange |  |
| XV3423 | Valve | CIP Return Valve at Ion Exchg | Directs CIP fluid back to CIP 2 system |  |

Devices in Wet Ingredient Storage

| XV2175 | Valve | T-2170 Discharge Valve – Ingred. U | Controls flow from T-2170 to reactor 4 |  |
| --- | --- | --- | --- | --- |

## Unit Operation Interactions

Gas Storage Unit Gaseous ingredients are received from the gas storage unit. This unit has direct control over the outlet side of the storage tanks in the gas storage unit.

Wet Ingredient Storage Unit Ingredient U is received from the wet ingredient storage unit. This unit has direct control over one of the valves in the wet ingredient storage unit.

Ion Exchange Cell Liquid product is transferred to the ion exchange cell from the reactor. If neither ion exchange 5 or 6 unit is ready, no new batches will be made.

Clean In Place 2 Unit Used to get rinse water to rinse reactor between batches.

## Reactor 4 Operational States

	Make Batch – Combines water and ingredient U and "bubbles" gas ingredient through the mixture to produce product. Do not allow this operation if Make Batch or Flush is in operation. Steps:

Check Reactor Level LI3400 < 1% and TI3400 < 80 deg. F and either Ion Exchange 5 or 6 online

Display prompt for operator and operator selects gas tank source

Close all valves (one step)

Add 1000 gal. of water:

Reset FQI3411

Open XV3411

Wait for FQI3411 >= 1000

Close XV3411

Start A-3400

Add 400 gal. of Ingredient U:

Reset FQI3402

Open XV3402

Open XV2175

Start P-3402

Wait for FQI3402 >= 400

Stop P-3402

Bubble 500 scfm gas through mixture:

Reset FQI3401

Open XV3401

Open XV3440

Open appropriate gas tank outlet valve, XV28x5

Wait for FQI3401 >= 500

Close XV28x5

Close XV3401

Close XV3440

Agitate for 10 minutes

If neither Ion Exchange 5 or 6 is Online,

Request Ion Exchange #5 to startup and wait for Ion Exchange #5 starting

Wait for Ion Exchange #5 online

Open XV3422

Open XV3400

Start P-3400

Wait for reactor level LI3400 < 1%

Stop A-3400

Stop P-3400

Close XV3400

Close XV3422

Initiate Flush

	Flush - Flushes reactor vessel and piping to ion exchange in preparation for next batch. Only allowed if reactor is at end of Make Batch or Shutdown.

Check Reactor Level LI3400 < 1%

Close all valves (one step)

If CIP_2 System is in shutdown or e-shutdown,

Request CIP_2 System to go online/recycle and wait for CIP_2 system online

Request CIP_2 System for Reactor 4 Path and wait for CIP_2 system Reactor 4 path set

Open XV3412

Wait for LI3400 >= 10%.

Start A-3400

Wait for LI3400 >= 95%.

Close XV3412

Agitate for 10 minutes

Open XV3423

Open XV3400

Start P-3400

Wait for LI3400 <= 1%

Stop A-3400

Request CIP_2 system to go online/recycle and wait for XV6203 to be closed

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Close XV2175

Stop P-3402

Close XV3402

Close all XV28x5 (all in one step)

Close XV3401

Close XV3411

Close XV3412

Stop A-3400

Stop P-3400

Close XV3400

Close XV3422

Close XV3423

Close XV3440

	E-Shutdown - Immediately turns off all pumps and all valves:

Close XV2175 and all XV28x5

Stop A-3400

Stop P-3400, P-3402

Close XV3401, XV3402, XV3411, XV3412, XV3400, XV3422, XV3423, XV3440

### Reactor 4 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI3400 > 96% for 20 seconds  Alarm

LI3400 > 98% for 20 seconds  Shut down process

LI3400 < 1% for 20 seconds while transferring product to ion exchange in progress  Shutdown

TI3400 >= 110 deg F for 20 seconds while making batch  Alarm

TI3400 >= 125 deg F for 20 seconds while making batch  Shutdown

AI3400 <= 5.0 or AI3400 >=9.0 for 20 seconds while making batch  Shutdown

Ion Exchange #5 and Ion Exchange #6 is not online when transferring product to ion exchange  E-Shutdown

CIP_2 System not in Reactor 4 Path when Reactor in steps where CIP_2 system used  E-Shutdown

Lose heartbeat with CIP_2 System for 10 seconds when Reactor in steps where CIP_2 system used  Hold

Ion Exchange #5 and Ion Exchange #6 not online when flushing product into ion exchange   E-Shutdown

Lose heartbeat with Ion Exchange #5 for 10 seconds and lose heartbeat with Ion Exchange #6  Hold

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Note: "While making batch" means "after 1000 gal. water added and reactor level > 5% while product transferred out of reactor"

# QA Sample Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-3800 | Product Analyzer | Analyzer that assesses product quality. |
| P-3810 | R1 Sample Pump | Bellows metering pump that transfers liquid product out of reactor 1 through analyzer and back to reactor 1. |
| P-3820 | R2 Sample Pump | Bellows metering pump that transfers liquid product out of reactor 2 through analyzer and back to reactor 2. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI3800 | Indicator | Analyzer measurement | Monitor major quality indicator in reactor product | 0-100 |  |
| FI3810 | Indicator | Reactor 1 sample inlet flow | Measures flow of sample | 0-4 gpm |  |
| FI3820 | Indicator | Reactor 2 sample inlet flow | Measures flow of sample | 0-4 gpm |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-3810 | Pump | R1 Sample Pump | Pumps sample from R1 |  |
| P-3820 | Pump | R2 Sample Pump | Pumps sample from R2 |  |
| XV3811 | Valve | Reactor 1 QA Sample Inlet Valve | Allows R1 contents to be transferred for quality sampling |  |
| XV3812 | Valve | Reactor 1 Path Hot Water Inlet Valve | Allows hot water to flush out reactor 1 path |  |
| XV3813 | Valve | Reactor 1 Analyzer Inlet Valve | Allows R1 contents to enter analyzer |  |
| XV3814 | Valve | Reactor 1 Analyzer Outlet Valve | Allows R1 contents to exit analyzer |  |
| XV3815 | Valve | Reactor 1 Sample Return Drain Valve | Drains path back to R1 |  |
| XV3816 | Valve | Reactor 1 Sample Return Valve | Returns sample to R1 |  |
| XV3821 | Valve | Reactor 2 QA Sample Inlet Valve | Allows R2 contents to be transferred for quality sampling |  |
| XV3822 | Valve | Reactor 2 Path Hot Water Inlet Valve | Allows hot water to flush out reactor 2 path |  |
| XV3823 | Valve | Reactor 2 Analyzer Inlet Valve | Allows R2 contents to enter analyzer |  |
| XV3824 | Valve | Reactor 2 Analyzer Outlet Valve | Allows R2 contents to exit analyzer |  |
| XV3825 | Valve | Reactor 2 Sample Return Drain Valve | Drains path back to R2 |  |
| XV3826 | Valve | Reactor 2 Sample Return Valve | Returns sample to R2 |  |
| XV3881 | Valve | Analyzer Outlet Drain Valve | Drains analyzer outlet |  |

## Unit Operation Interactions

Reactor Units When requested by a reactor unit, the valve paths are set to direct reactor contents to the analyzer system and then returned to the reactor.

## QA Sample Unit Operational States

	Sample R1 - Samples reactor 1 product. Extracts a sample from reactor 1 and initially sends it to the drain until analyzer reading has stabilized. Then the product is continuously sampled and returned to reactor 1. Do not allow this operation to start if sampling for reactor 2 and indication to reactor 2 has not been sent or if sampling system is locked to reactor 2. After indication is sent to reactor 1, the QA sampling system can be requested by reactor 2. Steps:

If Sample R2 in progress, close all valves (one step), stop P-3820

Open Reactor 1 QA sampling inlet, XV3811

Open R1 analyzer inlet, XV3813

Open analyzer drain, XV3881

Start R1 sample pump, P-3810

Wait 30 seconds (for sample to travel to analyzer)

Monitor AI3800, waiting for AI 3800 to stay within +/- 1.0 for 30 seconds

Set/latch "QA Sample finished" to reactor 1

Set/latch "Sample R1 in progress" (so Sample R2 can interrupt)

Open R1 analyzer outlet, XV3814

Open R1 sample return drain, XV3815

Close analyzer drain, XV3881

Wait 30 seconds (for sample to travel to sample return drain)

Open R1 sample return, XV3816

Close R1 sample return drain, XV3815

Reset/unlatch "Sample R1 in progress"

Reset/unlatch "QA Sample finished" to reactor 1

	Sample R2 - Samples reactor 2 product. Extracts a sample from reactor 2 and initially sends it to the drain until analyzer reading has stabilized. Then the product is continuously sampled and returned to reactor 2. Do not allow this operation to start if sampling for reactor 1 and indication to reactor 1 has not been sent or if sampling system is locked to reactor 1. After indication is sent to reactor 2, the QA sampling system can be requested by reactor 1. Steps:

If sampling reactor 1, close all valves (one step), stop P-3810

Open Reactor 2 QA sampling inlet, XV3821

Open R2 analyzer inlet, XV3823

Open analyzer drain, XV3881

Start R2 sample pump, P-3820

Wait 30 seconds (for sample to travel to analyzer)

Monitor AI3800, waiting for AI 3800 to stay within +/- 1.0 for 30 seconds

Set/latch "QA Sample finished" to reactor 2

Set/latch "Sample R2 in progress" (so Sample R1 can interrupt)

Open R2 analyzer outlet, XV3824

Open R2 sample return drain, XV3825

Close analyzer drain, XV3881

Wait 30 seconds (for sample to travel to sample return drain)

Open R2 sample return, XV3826

Close R2 sample return drain, XV3825

Reset/unlatch "Sample R2 in progress"

Reset/unlatch "QA Sample finished" to reactor 2

	Lock R1 - Locks sampling system to reactor 1. Extracts a sample from reactor 1 and initially sends it to the drain until analyzer reading has stabilized. Then the product is continuously sampled and returned to reactor 1. Do not allow this operation to start if sampling system is locked to reactor 2. Steps:

Set/latch "R1 locked"

Other steps same as "Sample Reactor 1"

	Lock R2 - Locks sampling system to reactor 2. Extracts a sample from reactor 2 and initially sends it to the drain until analyzer reading has stabilized. Then the product is continuously sampled and returned to reactor 2. Do not allow this operation to start if sampling system is locked to reactor 1. Steps:

Set/latch "R2 locked"

Same as "Sample Reactor 2"

	Unlock R1 - Cancel lock of sampling system to reactor 1. Only allowed if sampling system is locked to reactor 1. Steps:

Reset/unlatch "R1 locked"

Initiate shutdown

	Unlock R2 - Cancel lock of sampling system to reactor 2. Only allowed if sampling system is locked to reactor 2. Steps:

Reset/unlatch "R2 locked"

Initiate shutdown

	Flush R1 Path - Flush R1 sampling system with hot water. Only allowed if sampling system is already shutdown or E-shutdown:

Open XV3815

Open XV3814

Open XV3813

Open XV3812

Start P-3810

Flush for 5 minutes

Initiate shutdown

	Flush R2 Path - Flush R2 sampling system with hot water. Only allowed if sampling system is already shutdown or E-shutdown:

Open XV3825

Open XV3824

Open XV3823

Open XV3822

Start P-3820

Flush for 5 minutes

Initiate shutdown

	Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off the pumps and closes all valves:

Stop P-3810

Stop P-3820

Close XV3811

Close XV3821

Close XV3812

Close XV3822

Close XV3813

Close XV3823

Close XV3881

Close XV3814

Close XV3824

Close XV3815

Close XV3825

Close XV3816

Close XV3826

	E-Shutdown - Immediately turns off the pumps and closes all valves:

Stop P-3810, P-3820

Close XV3811, XV3821, XV3812, XV3822, XV3813, XV3823,

XV3881, XV3814, XV3824, XV3815, XV3825, XV3816, XV3826

### QA Sampling Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

If P-3810 is running and FI3810 < 0.1 gpm for 30 seconds  Alarm and Hold

If P-3810 is running and FI3810 < 0.1 gpm for 1 minute  Shutdown

If P-3820 is running and FI3820 < 0.1 gpm for 30 seconds  Alarm and Hold

If P-3820 is running and FI3820 < 0.1 gpm for 1 minute  Shutdown

Any pump failure for 30 seconds  Hold

Any valve failure for 30 seconds  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

Shutdown of unit using QA_Sample  Shutdown

Losing heartbeat with any unit using QA_Sample for 10 seconds  Shutdown

# Ion Exchange #1 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| T-4100 | Ion Exchange #1 Tank | 500 gallon tank to process the reactor product to remove some of the product impurities. |
| P-4102 | Regen Pump | Centrifugal pump that transfers regenerating liquid into the ion exchange tank. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI4100 | Indicator | Conductivity of Ion Exchange Tank | Monitor conductivity | 0-100 mmho/cm |  |
| FI4101 | Indicator | Product flow rate | Measures flow rate of product through ion exchange | 0-200 gpm |  |
| FQI4101 | Indicator | Totalized product in transfer flow | Measures amount of product from reactor being transferred through ion exchange |  |  |
| FIC4102 | Loop | Regen material transfer flow control | Controls flow rate of regen material to ion exchange vessel | 0-100 gpm, Fail closed, direct acting |  |
| FQI4102 | Indicator | Totalized regen material transfer flow | Measures amount of regen material being transferred to ion exchange |  |  |
| FIC4103 | Loop | Rinse water flow control | Controls feed rate of rinse water to ion exchanger | 0-100 gpm, Fail closed, direct acting |  |
| FQI4103 | Indicator | Totalized rinse water transfer flow | Measures amount of rinse water transferred to ion exchange |  |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-4102 | Motor | Regen Material Pump | Pumps regen material to ion exchanger | This pump should not run if PV:FIC4102<1.0 gpm and VO:FIC4102=100% |
| XV4101 | Valve | Ion Exchange #1 Product Inlet Valve | Controls flow of product into ion exchange tank |  |
| XV4102 | Valve | Ion Exchange #1 Regen Material Inlet Valve | Controls flow of regen into ion exchange tank |  |
| XV4103 | Valve | Rinse Water Feed Valve | Controls flow of rinse water into ion exchange |  |
| XV4105 | Valve | Ion Exchange #1 Product Discharge Valve | Controls flow of product out of ion exchange tank |  |
| XV4106 | Valve | Ion Exchange #1 Regen Material Discharge Valve | Controls flow of regen out of ion exchange tank |  |
| XV4107 | Valve | Rinse Water Discharge Valve | Controls flow of rinse water out of ion exchange |  |
| XV4121 | Valve | CIP to Ion Exchange Valve | Controls flow of CIP water into piping to QA Tank 1 |  |
| XV4122 | Valve | Product to QA Tank Xfer Valve | Controls flow of product to QA tank 1 |  |
| XV4123 | Valve | CIP Return Valve | Directs CIP water back to CIP System |  |

## Unit Operation Interactions

Reactor 1 and Reactor 2 Unit Liquid product is received from either reactor unit. This unit has no direct control over the reactor units.

CIP System The ion exchange unit requests CIP water. When CIP is granted, CIP water is directed to the ion exchange discharge pump, and the outlet piping valves are properly set to transfer the remaining product in the piping to the QA tank and then return the cleaning water to the CIP tank. When the flush is finished, then the CIP system is requested to return to its normal online/recycle operation.

Product Storage 1 Unit Liquid product is transferred to the QA tank 1 from the ion exchange unit. If the QA tank 1 is too full, the ion exchange unit is shutdown.

Regeneration Material Unit Used to get regeneration material to ion exchange for regeneration.

Rinse Water Unit Used to get rinse water to ion exchange after regeneration.

## Ion Exchange #1 Unit Operational States

	Startup – Starts up the online operation of ion exchange tank #1. Requested by operator or reactor unit. Steps:

Check Ion Exchange #1 Conductivity AI4100 < 50 mmho/cm

Close XV4102, XV4103, XV4106, XV4107, XV4121, XV4123

Reset FQI4101

Open XV4101

Open XV4105

Open XV4122

Initiate Online

	Online – Online operation of ion exchange tank #1. Steps:

When FQI4101 >= 100,000 gal., initiate Regenerating

	Regenerate – Regenerate ion exchange bed. Initiated by operator or if 100,000 gal. of product has passed through the ion exchange. Only allowed if both reactor 1 and reactor 2 are not in Make Batch. Steps:

Close XV4101, XV4103, XV4105, XV4107

Regenerate bed with 1500 gal. of regeneration material

Open XV4102

Open XV4106

Set Regen Material Flow Controller FIC4102 to manual, 20% output

Reset FQI4102

Start P-4102

Set Regen Material Flow Controller FIC4102 to auto, setpoint = 70 gpm

Wait for FQI4102 >= 1500 gal.

Stop P-4102

Set FIC4102 to manual, 0% output

Close XV4102

Close XV4106

Rinse bed with 2000 gal. of water

Reset FQI4103

Open XV4103

Open XV4107

Set Rinse Water Flow Controller FIC4103 to manual, 10% output

Set Rinse Water Flow Controller FIC4103 to auto, setpoint = 40 gpm

Wait for FQI4103 >= 1000 gal.

Set Rinse Water Flow Controller FIC4103 to auto, setpoint = 70 gpm

Wait for FQI4103 >= 2000 gal.

Set FIC4103 to manual, 0% output

Close XV4103

Close XV4107

Shutdown the system

	Flush - Flushes the piping to the QA tank 1. Can be requested if already shutdown:

If CIP_1 System is in shutdown or e-shutdown, request CIP_1 System to go online/recycle

Wait for CIP_1 system online

Request CIP_1 System to set Ion Exchange Path

Wait for CIP_1 system path set

Open QA tank feed valve XV4122

Open CIP_1 to ion exchange feed valve XV4121

Wait 2 minutes for product to be flushed into QA tank 1.

Open XV4123 and close XV4122 (one step)

Flush for 10 minutes

Request CIP_1 system to go online/recycle and wait for XV6004 to be closed

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Stop P-4102

Close XV4101

Set FIC4102 to manual, 0% output

Close XV4102

Set FIC4103 to manual, 0% output

Close XV4103

Close XV4105

Close XV4106

Close XV4107

Close XV4121

Close XV4122

Close XV4123

	E-Shutdown - Immediately turns off all pumps and all valves:

Stop P-4102

Set FIC4102 to manual, 0% output

Set FIC4103 to manual, 0% output

Close XV4101, XV4102, XV4103, XV4105, XV4106, XV4107, XV4121, XV4122, XV4123

### Ion Exchange #1 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

AI4100 > 50 mmho/cm  for 20 seconds  Alarm

AI4100 > 60 mmho/cm for 20 seconds  Shutdown process

Product Storage Tank 1 full  E-Shutdown

CIP_1 System not in Ion Exchange Outlet Path when Ion Exchange in steps where CIP_1 system used  E-Shutdown

Lose heartbeat with CIP_1 System for 10 seconds when Ion Exchange in steps where CIP_1 system used  E-Shutdown

Lose heartbeat with Stor_Tnk_1 System for 10 seconds  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Ion Exchange #2 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| T-4200 | Ion Exchange #2 Tank | 500 gallon tank to process the reactor product to remove some of the product impurities. |
| P-4202 | Regen Pump | Centrifugal pump that transfers regenerating liquid into the ion exchange tank. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI4200 | Indicator | Conductivity of Ion Exchange Tank | Monitor conductivity | 0-100 mmho/cm |  |
| FI4201 | Indicator | Product flow rate | Measures flow rate of product through ion exchange | 0-200 gpm |  |
| FQI4201 | Indicator | Totalized product in transfer flow | Measures amount of product from reactor being transferred through ion exchange |  |  |
| FIC4202 | Loop | Regen material transfer flow control | Controls flow rate of regen material to ion exchange vessel | 0-200 gpm, Fail closed, direct acting |  |
| FQI4202 | Indicator | Totalized regen material transfer flow | Measures amount of regen material being transferred to ion exchange |  |  |
| FIC4203 | Loop | Rinse water flow control | Controls feed rate of rinse water to ion exchanger | 0-200 gpm, Fail closed, direct acting |  |
| FQI4203 | Indicator | Totalized rinse water transfer flow | Measures amount of rinse water transferred to ion exchange |  |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-4202 | Motor | Regen Material Pump | Pumps regen material to ion exchanger | This pump should not run if PV:FIC4202<1.0 gpm and VO:FIC4202=100% |
| XV4201 | Valve | Ion Exchange #1 Product Inlet Valve | Controls flow of product into ion exchange tank |  |
| XV4202 | Valve | Ion Exchange #1 Regen Material Inlet Valve | Controls flow of regen into ion exchange tank |  |
| XV4203 | Valve | Rinse Water Feed Valve | Controls flow of rinse water into ion exchange |  |
| XV4205 | Valve | Ion Exchange #1 Product Discharge Valve | Controls flow of product out of ion exchange tank |  |
| XV4206 | Valve | Ion Exchange #1 Regen Material Discharge Valve | Controls flow of regen out of ion exchange tank |  |
| XV4207 | Valve | Rinse Water Discharge Valve | Controls flow of rinse water out of ion exchange |  |
| XV4221 | Valve | CIP_1 to Ion Exchange Valve | Controls flow of CIP_1 water into piping to QA Tank 1 |  |
| XV4222 | Valve | Product to QA Tank Xfer Valve | Controls flow of product to QA tank 1 |  |
| XV4223 | Valve | CIP_1 Return Valve | Directs CIP water back to CIP_1 System |  |

## Unit Operation Interactions

Reactor 1 and Reactor 2 Unit Liquid product is received from either reactor unit. This unit has no direct control over the reactor units.

CIP_1 System The ion exchange unit requests CIP_1 water. When CIP_1 is granted, CIP_1 water is directed to the ion exchange discharge pump, and the outlet piping valves are properly set to transfer the remaining product in the piping to the QA tank and then return the cleaning water to the CIP_1 tank. When the flush is finished, then the CIP_1 system is requested to return to its normal online/recycle operation.

Product Storage 1 Unit Liquid product is transferred to the QA tank 1 from the ion exchange unit. If the QA tank 1 is too full, the ion exchange unit is shutdown.

Regeneration Material Unit Used to get regeneration material to ion exchange for regeneration.

Rinse Water Unit Used to get rinse water to ion exchange after regeneration.

## Ion Exchange #2 Unit Operational States

	Startup – Starts up the online operation of ion exchange tank #2. Requested by operator or reactor unit. Steps:

Check Ion Exchange #2 Conductivity AI4200 < 50 mmho/cm

Close XV4202, XV4203, XV4206, XV4207, XV4221, XV4223

Reset FQI4201

Open XV4201

Open XV4205

Open XV4222

Initiate Online

	Online – Online operation of ion exchange tank #2. Steps:

When FQI4201 >= 100,000 gal., initiate Regenerating

	Regenerate – Regenerate ion exchange bed. Initiated by operator or if 100,000 gal. of product has passed through the ion exchange. Only allowed if both reactor 1 and reactor 2 are not in Make Batch. Steps:

Close XV4201, XV4203, XV4205, XV4207

Regenerate bed with 500 gal. of regeneration material

Open XV4202

Open XV4206

Set Regen Material Flow Controller FIC4202 to manual, 20% output

Reset FQI4202

Start P-4202

Set Regen Material Flow Controller FIC4202 to auto, setpoint = 150 gpm

Wait for FQI4202 >= 500 gal.

Stop P-4202

Set FIC4202 to manual, 0% output

Close XV4202

Close XV4206

Rinse bed with 1000 gal. of water

Reset FQI4203

Open XV4203

Open XV4207

Set Rinse Water Flow Controller FIC4203 to manual, 10% output

Set Rinse Water Flow Controller FIC4203 to auto, setpoint = 80 gpm

Wait for FQI4203 >= 500 gal.

Set Rinse Water Flow Controller FIC4203 to auto, setpoint = 140 gpm

Wait for FQI4203 >= 1000 gal.

Set FIC4203 to manual, 0% output

Close XV4203

Close XV4207

Shutdown the system

	Flush - Flushes the piping to the QA tank 1. Can be requested if already shutdown:

If CIP_1 System is in shutdown or e-shutdown, request CIP_1 System to go online/recycle

Wait for CIP_1 system online

Request CIP_1 System to set Ion Exchange Path

Wait for CIP_1 system path set

Open QA tank feed valve XV4222

Open CIP_1 to ion exchange feed valve XV4221

Wait 2 minutes for product to be flushed into QA tank 1.

Open XV4223 and close XV4222 (one step)

Flush for 10 minutes

Request CIP_1 system to go online/recycle and wait for XV6004 to be closed

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Stop P-4202

Close XV4201

Set FIC4202 to manual, 0% output

Close XV4202

Set FIC4203 to manual, 0% output

Close XV4203

Close XV4205

Close XV4206

Close XV4207

Close XV4221

Close XV4222

Close XV4223

	E-Shutdown - Immediately turns off all pumps and all valves:

Stop P-4202

Set FIC4202 to manual, 0% output

Set FIC4203 to manual, 0% output

Close XV4201, XV4202, XV4203, XV4205, XV4206, XV4207, XV4221, XV4222, XV4223

### Ion Exchange #2 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

AI4200 > 50 mmho/cm  for 20 seconds  Alarm

AI4200 > 60 mmho/cm for 20 seconds  Shutdown process

Product Storage Tank 1 full  E-Shutdown

CIP_1 System not in Ion Exchange Outlet Path when Ion Exchange in steps where CIP_1 system used  E-Shutdown

Lose heartbeat with CIP_1 System for 10 seconds when Ion Exchange in steps where CIP_1 system used  E-Shutdown

Lose heartbeat with Stor_Tnk_1 System for 10 seconds  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Ion Exchange #3 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| T-4300 | Ion Exchange #3 Tank | 500 gallon tank to process the reactor product to remove some of the product impurities. |
| P-4302 | Regen Pump | Centrifugal pump that transfers regenerating liquid into the ion exchange tank. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI4300 | Indicator | Conductivity of Ion Exchange Tank | Monitor conductivity | 0-100 mmho/cm |  |
| FI4301 | Indicator | Product flow rate | Measures flow rate of product through ion exchange | 0-200 gpm |  |
| FQI4301 | Indicator | Totalized product in transfer flow | Measures amount of product from reactor being transferred through ion exchange |  |  |
| FIC4302 | Loop | Regen material transfer flow control | Controls flow rate of regen material to ion exchange vessel | 0-100 gpm, Fail closed, direct acting |  |
| FQI4302 | Indicator | Totalized regen material transfer flow | Measures amount of regen material being transferred to ion exchange |  |  |
| FIC4303 | Loop | Rinse water flow control | Controls feed rate of rinse water to ion exchanger | 0-100 gpm, Fail closed, direct acting |  |
| FQI4303 | Indicator | Totalized rinse water transfer flow | Measures amount of rinse water transferred to ion exchange |  |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-4302 | Motor | Regen Material Pump | Pumps regen material to ion exchanger | This pump should not run if PV:FIC4302<1.0 gpm and VO:FIC4302=100% |
| XV4301 | Valve | Ion Exchange #3 Product Inlet Valve | Controls flow of product into ion exchange tank |  |
| XV4302 | Valve | Ion Exchange #3 Regen Material Inlet Valve | Controls flow of regen into ion exchange tank |  |
| XV4303 | Valve | Rinse Water Feed Valve | Controls flow of rinse water into ion exchange |  |
| XV4305 | Valve | Ion Exchange #3 Product Discharge Valve | Controls flow of product out of ion exchange tank |  |
| XV4306 | Valve | Ion Exchange #3 Regen Material Discharge Valve | Controls flow of regen out of ion exchange tank |  |
| XV4307 | Valve | Rinse Water Discharge Valve | Controls flow of rinse water out of ion exchange |  |
| XV4321 | Valve | Rinse to Ion Exchange Out Piping Valve | Controls flow of rinse water into piping to QA Tank 2 |  |
| XV4322 | Valve | Product to QA Tank Xfer Valve | Controls flow of product to QA tank 2 |  |
| XV4323 | Valve | Rinse Return Valve | Directs rinse water in piping to drain |  |

## Unit Operation Interactions

Reactor 3 Unit Liquid product is received from reactor unit. This unit has no direct control over the reactor units.

Product Storage 2 Unit Liquid product is transferred to the QA tank 2 from the ion exchange unit. If the QA tank 2 is too full, the ion exchange unit is shutdown.

Regeneration Material Unit Used to get regeneration material to ion exchange for regeneration.

Rinse Water Unit Used to get rinse water to ion exchange after regeneration.

## Ion Exchange #3 Unit Operational States

	Startup – Starts up the online operation of ion exchange tank #3. Requested by operator or reactor unit. Steps:

Check Ion Exchange #3 Conductivity AI4300 < 50 mmho/cm

Close XV4302, XV4303, XV4306, XV4307, XV4321, XV4323

Reset FQI4301

Open XV4301

Open XV4305

Open XV4322

Initiate Online

	Online – Online operation of ion exchange tank #3. Steps:

When FQI4301 >= 100,000 gal., initiate Regenerating

	Regenerate – Regenerate ion exchange bed. Initiated by operator or if 100,000 gal. of product has passed through the ion exchange. Only allowed if Reactor 3 is not in Make Batch. Steps:

Close XV4301, XV4303, XV4305, XV4307

Regenerate bed with 1500 gal. of regeneration material

Open XV4302

Open XV4306

Set Regen Material Flow Controller FIC4302 to manual, 20% output

Reset FQI4302

Start P-4302

Set Regen Material Flow Controller FIC4302 to auto, setpoint = 70 gpm

Wait for FQI4302 >= 1500 gal.

Stop P-4302

Set FIC4302 to manual, 0% output

Close XV4302

Close XV4306

Rinse bed with 2000 gal. of water

Reset FQI4303

Open XV4303

Open XV4307

Set Rinse Water Flow Controller FIC4303 to manual, 10% output

Set Rinse Water Flow Controller FIC4303 to auto, setpoint = 40 gpm

Wait for FQI4303 >= 1000 gal.

Set Rinse Water Flow Controller FIC4303 to auto, setpoint = 70 gpm

Wait for FQI4303 >= 2000 gal.

Set FIC4303 to manual, 0% output

Close XV4303

Close XV4307

Shutdown the system

	Flush - Flushes the piping to the QA tank 2. Can be requested if already shutdown:

Open QA tank feed valve XV4322

Open rinse to ion exchange out piping feed valve XV4321

Wait 2 minutes for product to be flushed into QA tank.

Open XV4323 and close XV4322 (one step)

Flush for 10 minutes

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Stop P-4302

Close XV4301

Set FIC4302 to manual, 0% output

Close XV4302

Set FIC4303 to manual, 0% output

Close XV4303

Close XV4305

Close XV4306

Close XV4307

Close XV4321

Close XV4322

Close XV4323

	E-Shutdown - Immediately turns off all pumps and all valves:

Stop P-4302

Set FIC4302 to manual, 0% output

Set FIC4303 to manual, 0% output

Close XV4301, XV4302, XV4303, XV4305, XV4306, XV4307, XV4321, XV4322, XV4323

### Ion Exchange #3 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

AI4300 > 50 mmho/cm  for 20 seconds  Alarm

AI4300 > 60 mmho/cm for 20 seconds  Shutdown process

Product Storage Tank 2 full  E-Shutdown

Lose heartbeat with Stor_Tnk_2 System for 10 seconds  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Ion Exchange #4 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| T-4400 | Ion Exchange #4 Tank | 500 gallon tank to process the reactor product to remove some of the product impurities. |
| P-4402 | Regen Pump | Centrifugal pump that transfers regenerating liquid into the ion exchange tank. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI4400 | Indicator | Conductivity of Ion Exchange Tank | Monitor conductivity | 0-100 mmho/cm |  |
| FI4401 | Indicator | Product flow rate | Measures flow rate of product through ion exchange | 0-200 gpm |  |
| FQI4401 | Indicator | Totalized product in transfer flow | Measures amount of product from reactor being transferred through ion exchange |  |  |
| FIC4402 | Loop | Regen material transfer flow control | Controls flow rate of regen material to ion exchange vessel | 0-100 gpm, Fail closed, direct acting |  |
| FQI4402 | Indicator | Totalized regen material transfer flow | Measures amount of regen material being transferred to ion exchange |  |  |
| FIC4403 | Loop | Rinse water flow control | Controls feed rate of rinse water to ion exchanger | 0-100 gpm, Fail closed, direct acting |  |
| FQI4403 | Indicator | Totalized rinse water transfer flow | Measures amount of rinse water transferred to ion exchange |  |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-4402 | Motor | Regen Material Pump | Pumps regen material to ion exchanger | This pump should not run if PV:FIC4402<1.0 gpm and VO:FIC4402=100% |
| XV4401 | Valve | Ion Exchange #4 Product Inlet Valve | Controls flow of product into ion exchange tank |  |
| XV4402 | Valve | Ion Exchange #4 Regen Material Inlet Valve | Controls flow of regen into ion exchange tank |  |
| XV4403 | Valve | Rinse Water Feed Valve | Controls flow of rinse water into ion exchange |  |
| XV4405 | Valve | Ion Exchange #4 Product Discharge Valve | Controls flow of product out of ion exchange tank |  |
| XV4406 | Valve | Ion Exchange #4 Regen Material Discharge Valve | Controls flow of regen out of ion exchange tank |  |
| XV4407 | Valve | Rinse Water Discharge Valve | Controls flow of rinse water out of ion exchange |  |
| XV4421 | Valve | Rinse to Ion Exchange Out Piping Valve | Controls flow of rinse water into piping to QA Tank 2 |  |
| XV4422 | Valve | Product to QA Tank Xfer Valve | Controls flow of product to QA tank 2 |  |
| XV4423 | Valve | Rinse Return Valve | Directs rinse water in piping to drain |  |

## Unit Operation Interactions

Reactor 3 Unit Liquid product is received from reactor unit. This unit has no direct control over the reactor units.

Product Storage 2 Unit Liquid product is transferred to the QA tank 2 from the ion exchange unit. If the QA tank 2 is too full, the ion exchange unit is shutdown.

Regeneration Material Unit Used to get regeneration material to ion exchange for regeneration.

Rinse Water Unit Used to get rinse water to ion exchange after regeneration and to flush piping.

## Ion Exchange #4 Unit Operational States

	Startup – Starts up the online operation of ion exchange tank #4. Requested by operator or reactor unit. Steps:

Check Ion Exchange #4 Conductivity AI4400 < 50 mmho/cm

Close XV4402, XV4403, XV4406, XV4407, XV4421, XV4423

Reset FQI4401

Open XV4401

Open XV4405

Open XV4422

Initiate Online

	Online – Online operation of ion exchange tank #4. Steps:

When FQI4401 >= 100,000 gal., initiate Regenerating

	Regenerate – Regenerate ion exchange bed. Initiated by operator or if 100,000 gal. of product has passed through the ion exchange. Only allowed if Reactor 3 is not in Make Batch. Steps:

Close XV4401, XV4403, XV4405, XV4407

Regenerate bed with 1500 gal. of regeneration material

Open XV4402

Open XV4406

Set Regen Material Flow Controller FIC4402 to manual, 20% output

Reset FQI4402

Start P-4402

Set Regen Material Flow Controller FIC4402 to auto, setpoint = 70 gpm

Wait for FQI4402 >= 1500 gal.

Stop P-4402

Set FIC4402 to manual, 0% output

Close XV4402

Close XV4406

Rinse bed with 2000 gal. of water

Reset FQI4403

Open XV4403

Open XV4407

Set Rinse Water Flow Controller FIC4403 to manual, 10% output

Set Rinse Water Flow Controller FIC4403 to auto, setpoint = 40 gpm

Wait for FQI4403 >= 1000 gal.

Set Rinse Water Flow Controller FIC4403 to auto, setpoint = 70 gpm

Wait for FQI4403 >= 2000 gal.

Set FIC4403 to manual, 0% output

Close XV4403

Close XV4407

Shutdown the system

	Flush - Flushes the piping to the QA tank 2. Can be requested if already shutdown:

Open QA tank feed valve XV4422

Open rinse to ion exchange out piping feed valve XV4421

Wait 2 minutes for product to be flushed into QA tank

Open XV4423 and close XV4422 (one step)

Flush for 10 minutes

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Stop P-4402

Close XV4401

Set FIC4402 to manual, 0% output

Close XV4402

Set FIC4403 to manual, 0% output

Close XV4403

Close XV4405

Close XV4406

Close XV4407

Close XV4421

Close XV4422

Close XV4423

	E-Shutdown - Immediately turns off all pumps and all valves:

Stop P-4402

Set FIC4402 to manual, 0% output

Set FIC4403 to manual, 0% output

Close XV4401, XV4402, XV4403, XV4405, XV4406, XV4407, XV4421, XV4422, XV4423

### Ion Exchange #4 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

AI4400 > 50 mmho/cm  for 20 seconds  Alarm

AI4400 > 60 mmho/cm for 20 seconds  Shutdown process

Product Storage Tank 2 full  E-Shutdown

Lose heartbeat with Stor_Tnk_2 System for 10 seconds  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Ion Exchange #5 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| T-4500 | Ion Exchange #5 Tank | 400 gallon tank to process the reactor product to remove some of the product impurities. |
| P-4502 | Regen Pump | Centrifugal pump that transfers regenerating liquid into the ion exchange tank. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI4500 | Indicator | Conductivity of Ion Exchange Tank | Monitor conductivity | 0-100 mmho/cm |  |
| FI4501 | Indicator | Product flow rate | Measures flow rate of product through ion exchange | 0-200 gpm |  |
| FQI4501 | Indicator | Totalized product in transfer flow | Measures amount of product from reactor being transferred through ion exchange |  |  |
| FIC4502 | Loop | Regen material transfer flow control | Controls flow rate of regen material to ion exchange vessel | 0-100 gpm, Fail closed, direct acting |  |
| FQI4502 | Indicator | Totalized regen material transfer flow | Measures amount of regen material being transferred to ion exchange |  |  |
| FIC4503 | Loop | Rinse water flow control | Controls feed rate of rinse water to ion exchanger | 0-100 gpm, Fail closed, direct acting |  |
| FQI4503 | Indicator | Totalized rinse water transfer flow | Measures amount of rinse water transferred to ion exchange |  |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-4502 | Motor | Regen Material Pump | Pumps regen material to ion exchanger | This pump should not run if PV:FIC4502<1.0 gpm and VO:FIC4502=100% |
| XV4501 | Valve | Ion Exchange #5 Product Inlet Valve | Controls flow of product into ion exchange tank |  |
| XV4502 | Valve | Ion Exchange #5 Regen Material Inlet Valve | Controls flow of regen into ion exchange tank |  |
| XV4503 | Valve | Rinse Water Feed Valve | Controls flow of rinse water into ion exchange |  |
| XV4505 | Valve | Ion Exchange #5 Product Discharge Valve | Controls flow of product out of ion exchange tank |  |
| XV4506 | Valve | Ion Exchange #5 Regen Material Discharge Valve | Controls flow of regen out of ion exchange tank |  |
| XV4507 | Valve | Rinse Water Discharge Valve | Controls flow of rinse water out of ion exchange |  |
| XV4521 | Valve | CIP_2 to Ion Exchange Out Piping Valve | Controls flow of CIP_2 fluid into piping to QA Tank 3 |  |
| XV4522 | Valve | Product to QA Tank Xfer Valve | Controls flow of product to QA tank 3 |  |
| XV4523 | Valve | CIP_2 Return Valve | Directs CIP_2 fluid in piping to drain |  |

## Unit Operation Interactions

Reactor 4 Unit Liquid product is received from reactor unit. This unit has no direct control over the reactor units.

CIP_2 System The ion exchange unit requests CIP_2 water. When CIP_2 is granted, CIP_2 water is directed to the ion exchange discharge pump, and the outlet piping valves are properly set to transfer the remaining product in the piping to the QA tank and then return the cleaning water to the CIP_2 tank. When the flush is finished, then the CIP_2  system is requested to return to its normal online/recycle operation.

Product Storage 3 Unit Liquid product is transferred to the QA tank 3 from the ion exchange unit. If the QA tank 3 is too full, the ion exchange unit is shutdown.

Regeneration Material Unit Used to get regeneration material to ion exchange for regeneration.

Rinse Water Unit Used to get rinse water to ion exchange after regeneration.

## Ion Exchange #5 Unit Operational States

	Startup – Starts up the online operation of ion exchange tank #5. Requested by operator or reactor unit. Steps:

Check Ion Exchange #5 Conductivity AI4500 < 50 mmho/cm

Close XV4502, XV4503, XV4506, XV4507, XV4521, XV4523

Reset FQI4501

Open XV4501

Open XV4505

Open XV4522

Initiate Online

	Online – Online operation of ion exchange tank #5. Steps:

When FQI4501 >= 50,000 gal., initiate Regenerating

	Regenerate – Regenerate ion exchange bed. Initiated by operator or if 50,000 gal. of product has passed through the ion exchange. Only allowed if Reactor 4 is not in Make Batch. Steps:

Close XV4501, XV4503, XV4505, XV4507

Regenerate bed with 1000 gal. of regeneration material

Open XV4502

Open XV4506

Set Regen Material Flow Controller FIC4502 to manual, 20% output

Reset FQI4502

Start P-4502

Set Regen Material Flow Controller FIC4502 to auto, setpoint = 70 gpm

Wait for FQI4502 >= 1000 gal.

Stop P-4502

Set FIC4502 to manual, 0% output

Close XV4502

Close XV4506

Rinse bed with 2000 gal. of water

Reset FQI4503

Open XV4503

Open XV4507

Set Rinse Water Flow Controller FIC4503 to manual, 10% output

Set Rinse Water Flow Controller FIC4503 to auto, setpoint = 40 gpm

Wait for FQI4503 >= 1000 gal.

Set Rinse Water Flow Controller FIC4503 to auto, setpoint = 70 gpm

Wait for FQI4503 >= 2000 gal.

Set FIC4503 to manual, 0% output

Close XV4503

Close XV4507

Shutdown the system

	Flush - Flushes the piping to the QA tank 3. Can be requested if already shutdown:

Open QA tank feed valve XV4522

If CIP_2 System is in shutdown or e-shutdown,

Request CIP_2 System to go online/recycle and wait for CIP_2 system online

Request CIP_2 to set path to ion exchange and wait for path set

Open CIP_2 fluid to ion exchange out piping feed valve XV4521

Wait 2 minutes for product to be flushed into QA tank.

Open XV4523 and close XV4522 (one step)

Flush for 10 minutes

Request CIP_2 system to go online/recycle and wait for XV6204 closed

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Stop P-4502

Close XV4501

Set FIC4502 to manual, 0% output

Close XV4502

Set FIC4503 to manual, 0% output

Close XV4503

Close XV4505

Close XV4506

Close XV4507

Close XV4521

Close XV4522

Close XV4523

	E-Shutdown - Immediately turns off all pumps and all valves:

Stop P-4502

Set FIC4502 to manual, 0% output

Set FIC4503 to manual, 0% output

Close XV4501, XV4502, XV4503, XV4505, XV4506, XV4507, XV4521, XV4522, XV4523

### Ion Exchange #5 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

AI4500 > 50 mmho/cm  for 20 seconds  Alarm

AI4500 > 60 mmho/cm for 20 seconds  Shutdown process

CIP_2 System not in Ion Exchange Path when Ion_Exc_5 in steps where CIP_2 system used  E-Shutdown

Lose heartbeat with CIP_2 System for 10 seconds when Ion Exchange in steps where CIP_2 system used  E-Shutdown

Product Storage Tank 3 full  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Ion Exchange #6 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| T-4600 | Ion Exchange #6 Tank | 400 gallon tank to process the reactor product to remove some of the product impurities. |
| P-4602 | Regen Pump | Centrifugal pump that transfers regenerating liquid into the ion exchange tank. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI4600 | Indicator | Conductivity of Ion Exchange Tank | Monitor conductivity | 0-100 mmho/cm |  |
| FI4601 | Indicator | Product flow rate | Measures flow rate of product through ion exchange | 0-200 gpm |  |
| FQI4601 | Indicator | Totalized product in transfer flow | Measures amount of product from reactor being transferred through ion exchange |  |  |
| FIC4602 | Loop | Regen material transfer flow control | Controls flow rate of regen material to ion exchange vessel | 0-100 gpm, Fail closed, direct acting |  |
| FQI4602 | Indicator | Totalized regen material transfer flow | Measures amount of regen material being transferred to ion exchange |  |  |
| FIC4603 | Loop | Rinse water flow control | Controls feed rate of rinse water to ion exchanger | 0-100 gpm, Fail closed, direct acting |  |
| FQI4603 | Indicator | Totalized rinse water transfer flow | Measures amount of rinse water transferred to ion exchange |  |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-4602 | Motor | Regen Material Pump | Pumps regen material to ion exchanger | This pump should not run if PV:FIC4602<1.0 gpm and VO:FIC4602=100% |
| XV4601 | Valve | Ion Exchange #6 Product Inlet Valve | Controls flow of product into ion exchange tank |  |
| XV4602 | Valve | Ion Exchange #6 Regen Material Inlet Valve | Controls flow of regen into ion exchange tank |  |
| XV4603 | Valve | Rinse Water Feed Valve | Controls flow of rinse water into ion exchange |  |
| XV4605 | Valve | Ion Exchange #6 Product Discharge Valve | Controls flow of product out of ion exchange tank |  |
| XV4606 | Valve | Ion Exchange #6 Regen Material Discharge Valve | Controls flow of regen out of ion exchange tank |  |
| XV4607 | Valve | Rinse Water Discharge Valve | Controls flow of rinse water out of ion exchange |  |
| XV4621 | Valve | CIP_2 to Ion Exchange Out Piping Valve | Controls flow of CIP_2 fluid into piping to QA Tank 3 |  |
| XV4622 | Valve | Product to QA Tank Xfer Valve | Controls flow of product to QA tank 3 |  |
| XV4623 | Valve | CIP_2 Return Valve | Directs CIP_2 fluid in piping to drain |  |

## Unit Operation Interactions

Reactor 4 Unit Liquid product is received from reactor unit. This unit has no direct control over the reactor units.

CIP_2 System The ion exchange unit requests CIP_2 water. When CIP_2 is granted, CIP_2 water is directed to the ion exchange discharge pump, and the outlet piping valves are properly set to transfer the remaining product in the piping to the QA tank and then return the cleaning water to the CIP_2 tank. When the flush is finished, then the CIP_2  system is requested to return to its normal online/recycle operation.

Product Storage 3 Unit Liquid product is transferred to the QA tank 3 from the ion exchange unit. If the QA tank 3 is too full, the ion exchange unit is shutdown.

Regeneration Material Unit Used to get regeneration material to ion exchange for regeneration.

Rinse Water Unit Used to get rinse water to ion exchange after regeneration and to flush piping.

## Ion Exchange #6 Unit Operational States

	Startup – Starts up the online operation of ion exchange tank #6. Requested by operator or reactor unit. Steps:

Check Ion Exchange #6 Conductivity AI4600 < 50 mmho/cm

Close XV4602, XV4603, XV4606, XV4607, XV4621, XV4623

Reset FQI4601

Open XV4601

Open XV4605

Open XV4622

Initiate Online

	Online – Online operation of ion exchange tank #6. Steps:

When FQI4601 >= 50,000 gal., initiate Regenerating

	Regenerate – Regenerate ion exchange bed. Initiated by operator or if 50,000 gal. of product has passed through the ion exchange. Only allowed if Reactor 4 is not in Make Batch. Steps:

Close XV4601, XV4603, XV4605, XV4607

Regenerate bed with 1000 gal. of regeneration material

Open XV4602

Open XV4606

Set Regen Material Flow Controller FIC4602 to manual, 20% output

Reset FQI4602

Start P-4602

Set Regen Material Flow Controller FIC4602 to auto, setpoint = 70 gpm

Wait for FQI4602 >= 1500 gal.

Stop P-4602

Set FIC4602 to manual, 0% output

Close XV4602

Close XV4606

Rinse bed with 2000 gal. of water

Reset FQI4603

Open XV4603

Open XV4607

Set Rinse Water Flow Controller FIC4603 to manual, 10% output

Set Rinse Water Flow Controller FIC4603 to auto, setpoint = 40 gpm

Wait for FQI4603 >= 1000 gal.

Set Rinse Water Flow Controller FIC4603 to auto, setpoint = 70 gpm

Wait for FQI4603 >= 2000 gal.

Set FIC4603 to manual, 0% output

Close XV4603

Close XV4607

Shutdown the system

	Flush - Flushes the piping to the QA tank 3. Can be requested if already shutdown:

Open QA tank feed valve XV4622

If CIP_2 System is in shutdown or e-shutdown,

Request CIP_2 System to go online/recycle and wait for CIP_2 system online

Request CIP_2 to set path to ion exchange and wait for path set

Open CIP_2 fluid to ion exchange out piping feed valve XV4621

Wait 2 minutes for product to be flushed into QA tank

Open XV4623 and close XV4622 (one step)

Flush for 10 minutes

Request CIP_2 system to go online/recycle and wait for XV6204 closed

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off all pumps and all valves:

Stop P-4602

Close XV4601

Set FIC4602 to manual, 0% output

Close XV4602

Set FIC4603 to manual, 0% output

Close XV4603

Close XV4605

Close XV4606

Close XV4607

Close XV4621

Close XV4622

Close XV4623

	E-Shutdown - Immediately turns off all pumps and all valves:

Stop P-4602

Set FIC4602 to manual, 0% output

Set FIC4603 to manual, 0% output

Close XV4601, XV4602, XV4603, XV4605, XV4606, XV4607, XV4621, XV4622, XV4623

### Ion Exchange #6 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

AI4600 > 50 mmho/cm  for 20 seconds  Alarm

AI4600 > 60 mmho/cm for 20 seconds  Shutdown process

CIP_2 System not in Ion Exchange Path when Ion_Exc_6 in steps where CIP_2 system used  E-Shutdown

Lose heartbeat with CIP_2 System for 10 seconds when Ion Exchange in steps where CIP_2 system used  E-Shutdown

Product Storage Tank 3 full  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Product Storage 1 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-5100 | QA Tank agitator | Mix the liquid product in the QA tank to keep uniform |
| F-5102 | Product filter | Removes impurities from product. |
| P-5101 | QA Pump | Centrifugal pump that transfers liquid product from QA tank into any storage tank. |
| T-5100 | QA Tank | 10,000 gallon storage tank to collect product. When enough product is in the tank and product meets QA specifications, it is transferred to one of the storage tanks. |
| T-5110 | Storage Tank #1 | 10,000 gallon storage tank. Product may be stored here until transferred to the truck/rail loadout. |
| T-5120 | Storage Tank #2 | 10,000 gallon storage tank. Product may be stored here until transferred to the truck/rail loadout. |
| T-5130 | Storage Tank #3 | 10,000 gallon storage tank. Product may be stored here until transferred to the truck/rail loadout. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| DPI5102 | Indicator | Pressure drop across F-5102 filters | Monitors pressure drop to indicate when filters need to be changed | 0-150” |  |
| LI5100 | Indicator | Level of QA Tank 1 | Monitor level | 0-100 (units %) |  |
| LI5110 | Indicator | Level of Storage Tank #1 | Monitor level | 0-100 (units %) |  |
| LI5120 | Indicator | Level of Storage Tank #2 | Monitor level | 0-100 (units %) |  |
| LI5130 | Indicator | Level of Storage Tank #3 | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-5100 | Motor | QA tank 1 agitator | Mixes liquid product in QA tank | Automatic on/off control with deadband. Off when level falls below 10%, On when level rises above 15% |
| P-5101 | Motor | QA 1 Pump | Pumps liquid product from QA tank into any storage tank | This pump should not run if: LI5100<2% or DPI5102>140” |
| XV5100 | Valve | QA Tank 1 Discharge Valve | Controls flow out of QA Tank |  |
| XV5l1l | Valve | Storage Tank #1 Feed Valve | Controls flow into Storage Tank #1 |  |
| XV5121 | Valve | Storage Tank #2 Feed Valve | Controls flow into Storage Tank #2 |  |
| XV5131 | Valve | Storage Tank #3 Feed Valve | Controls flow into Storage Tank #3 |  |
| XV5180 | Valve | Loadout Header CIP_1 Return Valve | Returns liquid flushed through header to CIP_1 |  |

## Unit Operation Interactions

Ion Exchange Unit Liquid product is received from the ion exchange #1 and #2 units into the QA tank 1. This unit has no control over the ion exchange units, except to shut them down when the QA level gets too high.

CIP 1 System The product storage unit requests CIP_1 water. When CIP_1 is granted, CIP_1 water is directed to the QA discharge pump, and the storage header valves are properly set to transfer the remaining product in the header to one of the tanks and then return the cleaning water to the CIP_1 tank. When the flush is finished, then the CIP_1 system is requested to return to its normal online/recycle operation.

Storage Loadout 1 Unit When requested by the operator, the product from one of the tanks, is directed to one of the stations in the truck/rail loadout 1.

## Product Storage 1 Operational States

	Transfer - Transfers the entire contents of the QA tank 1 to desired destination tank. Do not allow this operation to start if Transfer is in operation. Steps:

Ask for operator verification that destination selected

Check QA Tank Level > 5%

If destination tank is more than 80% full, abort operation (jump to last step)

Close all valves

Open appropriate tank inlet valve (XV5111, XV5121, or XV5131)

Open XV5100

Start P-5101

Wait until destination tank is full (level > 95%), or QA Tank is empty (level < 3%)

Shut down the system

	Flush - Flushes the storage tank header with CIP 1 water. Can only be requested if already shutdown

If QA tank level < 5% (enough to recharge product header), abort (go to last step)

If CIP_1 System is in shutdown or e-shutdown,

Request CIP_1 System to go online/recycle and wait for CIP_1 system online

Request CIP_1 System to set Feed Storage Path and wait for CIP_1 path set

If Storage Tank #3 has a level < 90%, open feed valve to tank #3 XV5131. Otherwise, open CIP_1 return valve XV5180

Start P-5101

If XV5131 opened, wait 45 seconds for product to be flushed into tank #3. Then open XV5180 and close XV5131

Flush for 10 minutes

Request CIP_1 system to go online/recycle and wait for XV6002 to be closed

Open XV5100

Charge product storage header with product (90 seconds)

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off the pump and all storage header valves:

Stop P-5101

Close XV5100

Close XV5111

Close XV5121

Close XV5131

Close XV5180

	E-Shutdown - Immediately turns off the pump and all storage header valves:

Stop P-5101

Close XV5100, XV5111, XV5121, XV5131, XV5180

### Product Storage 1 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI5100 > 90 (units in %) for 20 seconds  Alarm

LI5100 > 95% for 20 seconds  Shut down process (not implemented)

LI5100 < 2% for 20 seconds while transfer in progress  Shutdown

DPI5102 > 130” for 1 second  Alarm

DPI5102 > 140” for 1 second  Shutdown

LI5110 > 95% for 60 seconds while in transfer to T-5110  Shutdown

LI5120 > 95% for 60 seconds while in transfer to T-5120  Shutdown

LI5130 > 95% for 60 seconds while in transfer to T-5130   Shutdown

CIP_1 System not in Feed Storage Path when unit in steps where CIP_1 system used  E-Shutdown

Lose heartbeat with CIP_1 System for 10 seconds when unit in steps where CIP_1 system used  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Storage 1 Loadout Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| P-5181 | Loadout Pump | Centrifugal pump that transfers liquid product from any storage tank to the truck/rail loadout 1 |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| FIC5181 | Loop | Loadout transfer flow control | Controls feed rate of transfer to truck/rail loadout 1 | 0-200 gpm, Fail closed, direct acting |  |
| FQI5181 | Indicator | Totalized loadout product flow | Measures amount of product transferred to loadout 1 |  |  |
| LI5110 | Indicator | Level of Storage Tank #1 | Monitor level | 0-100 (units %) |  |
| LI5120 | Indicator | Level of Storage Tank #2 | Monitor level | 0-100 (units %) |  |
| LI5130 | Indicator | Level of Storage Tank #3 | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-5181 | Motor | Loadout Pump | Pumps liquid product from any storage tank to the truck/rail loadout 1 | This pump should not run if PV:FIC5200<0.5 gpm and VO:FIC5200=100% |
| XV5112 | Valve | Storage Tank #1 Discharge Valve | Controls flow out of Storage Tank #1 |  |
| XV5122 | Valve | Storage Tank #2 Discharge Valve | Controls flow out of Storage Tank #2 |  |
| XV5132 | Valve | Storage Tank #3 Discharge Valve | Controls flow out of Storage Tank #3 |  |
| XV5191 | Valve | Truck Load Station #1 Valve | Controls flow into truck at station #1 |  |
| XV5192 | Valve | Truck Load Station #2 Valve | Controls flow into truck at station #2 |  |
| XV5196 | Valve | Rail Load Station #1 Valve | Controls flow into railcar at station #1 |  |
| XV5197 | Valve | Rail Load Station #2 Valve | Controls flow into railcar at station #2 |  |

## Unit Operation Interactions

Storage Unit 1 This unit loads out product from the product storage 1 unit. This unit has no control over the product storage 1 unit.

## Storage 1 Loadout Unit Operational States

	Transfer - Transfers the entire contents of source tank to the desired station:

Ask for operator verification that source and destination selected

If source tank is less than 3% full, abort operation

Close all valves

(Start up loadout system)

Reset loadout flow totalizer, FQI5181

Request amount of product from operator

Open appropriate load station valve (XV5191, XV5192, XV5196, or XV5197)

Open appropriate tank outlet valve (XV5112, XV5122, or XV5132)

Start P-5181

Initialize the loadout flow controller to operator-adjusted setpoint

Wait until source tank is empty (level <3%) or FQI5181 totalized flow >= desired

Shut down the system

	Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off the pump and all discharge header valves:

Stop P-5181

Set FIC5181 to manual, -10% output

Close XV5112

Close XV5122

Close XV5132

Close XV5191

Close XV5192

Close XV5196

Close XV5197

	E-Shutdown - Immediately turns off the pump and all discharge header valves:

Stop P-5181

Set FIC5181 to manual, -10% output

Close XV5112, XV5122, XV5132, XV5191, XV5192, XV5196, XV5197

### Storage 1 Loadout Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI5110 < 3% for 20 seconds and T5110 Transfer in progress  Shut down

LI5120 < 3% for 20 seconds and T5120 Transfer in progress  Shut down

LI5130 < 3% for 20 seconds and T5130 Transfer in progress  Shut down

FI5181 deviates from setpoint by more than 2 gpm for 10 seconds while transfer in progress  Alarm

FI5181 deviates from setpoint by more than 2 gpm for 3 minutes while transfer in progress  Shutdown

FI5181 deviates from setpoint by more than 2 gpm for 2 seconds and FY5181 = 100% while transfer in progress  Shutdown (blocked valve in loadout)

FI5181 < 0.5 gpm and FY5181 = 100% for 2 seconds  Shutdown (pump protection)

Any pump failure  Hold

Any valve failure  Hold

#### Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Product Storage 2 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-5200 | QA Tank 2 agitator | Mix the liquid product in the QA tank to keep uniform |
| F-5202 | Product filter | Removes impurities from product. |
| P-5201 | QA Pump 2 | Centrifugal pump that transfers liquid product from QA tank into any storage tank. |
| T-5200 | QA Tank 2 | 10,000 gallon storage tank to collect product. When enough product is in the tank and product meets QA specifications, it is transferred to one of the storage tanks. |
| T-5210 | Storage Tank #21 | 10,000 gallon storage tank. Product may be stored here until transferred to the truck/rail loadout. |
| T-5220 | Storage Tank #22 | 10,000 gallon storage tank. Product may be stored here until transferred to the truck/rail loadout. |
| T-5230 | Storage Tank #23 | 10,000 gallon storage tank. Product may be stored here until transferred to the truck/rail loadout. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| DPI5202 | Indicator | Pressure drop across F-5202 filters | Monitors pressure drop to indicate when filters need to be changed | 0-150” |  |
| LI5200 | Indicator | Level of QA Tank 2 | Monitor level | 0-100 (units %) |  |
| LI5210 | Indicator | Level of Storage Tank #11 | Monitor level | 0-100 (units %) |  |
| LI5220 | Indicator | Level of Storage Tank #12 | Monitor level | 0-100 (units %) |  |
| LI5230 | Indicator | Level of Storage Tank #13 | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-5200 | Motor | QA tank 2 agitator | Mixes liquid product in QA tank | Automatic on/off control with deadband. Off when level falls below 10%, On when level rises above 15% |
| P-5201 | Motor | QA Pump 2 | Pumps liquid product from QA tank into any storage tank | This pump should not run if: LI5500<2% or DPI5600>140” |
| XV5200 | Valve | QA Tank 2 Discharge Valve | Controls flow out of QA Tank |  |
| XV5203 | Valve | Loadout Header Rinse Inlet Valve | Admits liquid flushed through header |  |
| XV521l | Valve | Storage Tank #21 Feed Valve | Controls flow into Storage Tank #21 |  |
| XV5221 | Valve | Storage Tank #22 Feed Valve | Controls flow into Storage Tank #22 |  |
| XV5231 | Valve | Storage Tank #23 Feed Valve | Controls flow into Storage Tank #23 |  |
| XV5280 | Valve | Loadout Header Rinse Return Valve | Returns liquid flushed through header to drain |  |

## Unit Operation Interactions

Ion Exchange #3 and #4 Units Liquid product is received from the ion exchange #3 and $4 units into the QA tank 2. This unit has no control over the ion exchange units, except to shut them down when the QA level 2 gets too high.

Rinse Water Unit Used to get rinse water to flush piping.

Storage Loadout 2 Unit When requested by the operator, the product from one of the tanks, is directed to one of the stations in the truck/rail loadout 2.

## Product Storage 2 Operational States

	Transfer - Transfers the entire contents of the QA tank 2 to desired destination tank. Do not allow this operation to start if Transfer is in operation. Steps:

Ask for operator verification that destination selected

Check QA Tank Level > 5%

If destination tank is more than 80% full, abort operation (jump to last step)

Close all valves

Open appropriate tank inlet valve (XV52x1)

Open XV5200

Start P-5201

Wait until destination tank is full (level > 95%), or QA Tank 2 is empty (level < 3%)

Shut down the system

	Flush - Flushes the storage tank header with rinse water. Can only be requested if already shutdown

If QA tank level < 5% (enough to recharge product header), abort (go to last step)

Open XV5203

If Storage Tank #23 has a level < 90%, open feed valve to tank #23 XV5231. Otherwise, open rinse return valve XV5280

Start P-5201

If XV5231 opened, wait 45 seconds for product to be flushed into tank #23. Then open XV5280 and close XV5231

Flush for 10 minutes

Close XV5203

Open XV5200

Charge product storage header with product (90 seconds)

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off the pump and all storage header valves:

Stop P-5201

Close XV5200

Close XV5203

Close XV5211

Close XV5221

Close XV5231

Close XV5280

	E-Shutdown - Immediately turns off the pump and all storage header valves:

Stop P-5201

Close XV5200, XV5203, XV5211, XV5221, XV5231, XV5280

### Product Storage 2 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI5200 > 90 (units in %) for 20 seconds  Alarm

LI5200 > 95% for 20 seconds  Shut down process (not implemented)

LI5200 < 2% for 20 seconds while transfer in progress  Shutdown

DPI5202 > 130” for 1 second  Alarm

DPI5202 > 140” for 1 second  Shutdown

LI5210 > 95% for 60 seconds while in transfer to T-5210  Shutdown

LI5220 > 95% for 60 seconds while in transfer to T-5220  Shutdown

LI5230 > 95% for 60 seconds while in transfer to T-5230   Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Storage 2 Loadout Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| P-5281 | Loadout Pump | Centrifugal pump that transfers liquid product from any storage tank to the truck/rail loadout 2 |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| FIC5281 | Loop | Loadout transfer flow control | Controls feed rate of transfer to truck/rail loadout 2 | 0-200 gpm, Fail closed, direct acting |  |
| FQI5281 | Indicator | Totalized loadout product flow | Measures amount of product transferred to loadout 2 |  |  |
| LI5210 | Indicator | Level of Storage Tank #21 | Monitor level | 0-100 (units %) |  |
| LI5220 | Indicator | Level of Storage Tank #22 | Monitor level | 0-100 (units %) |  |
| LI5230 | Indicator | Level of Storage Tank #23 | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-5281 | Motor | Loadout Pump | Pumps liquid product from any storage tank to the truck/rail loadout | This pump should not run if PV:FIC5281<0.5 gpm and VO:FIC5281=100% |
| XV5212 | Valve | Storage Tank #21 Discharge Valve | Controls flow out of Storage Tank #21 |  |
| XV5222 | Valve | Storage Tank #22 Discharge Valve | Controls flow out of Storage Tank #22 |  |
| XV5232 | Valve | Storage Tank #23 Discharge Valve | Controls flow out of Storage Tank #23 |  |
| XV5291 | Valve | Truck Load Station #1 Valve | Controls flow into truck at station #1 |  |
| XV5292 | Valve | Truck Load Station #2 Valve | Controls flow into truck at station #2 |  |
| XV5296 | Valve | Rail Load Station #1 Valve | Controls flow into railcar at station #1 |  |
| XV5297 | Valve | Rail Load Station #2 Valve | Controls flow into railcar at station #2 |  |

## Unit Operation Interactions

Storage Unit This unit loads out product from the product storage unit. This unit has no control over the product storage unit.

## Storage 2 Loadout Unit Operational States

	Transfer - Transfers the entire contents of source tank to the desired station:

Ask for operator verification that source and destination selected

If source tank is less than 3% full, abort operation

Close all valves

(Start up loadout system)

Reset loadout flow totalizer, FQI5281

Request amount of product from operator

Open appropriate load station valve (XV5291, XV5292, XV5296, or XV5297)

Open appropriate tank outlet valve (XV52x2)

Start P-5281

Initialize the loadout flow controller to operator-adjusted setpoint

Wait until source tank is empty (level <3%) or FQI5281 totalized flow >= desired

Shut down the system

	Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off the pump and all discharge header valves:

Stop P-5281

Set FIC5281 to manual, -10% output

Close XV5212

Close XV5222

Close XV5232

Close XV5291

Close XV5292

Close XV5296

Close XV5297

	E-Shutdown - Immediately turns off the pump and all discharge header valves:

Stop P-5281

Set FIC5281 to manual, -10% output

Close XV5212, XV5222, XV5232, XV5291, XV5292, XV5296, XV5297

### Storage 2 Loadout Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI5210 < 3% for 20 seconds and T5210 Transfer in progress  Shut down

LI5220 < 3% for 20 seconds and T5220 Transfer in progress  Shut down

LI5230 < 3% for 20 seconds and T5230 Transfer in progress  Shut down

FI5281 deviates from setpoint by more than 2 gpm for 10 seconds while transfer in progress  Alarm

FI5281 deviates from setpoint by more than 2 gpm for 3 minutes while transfer in progress  Shutdown

FI5281 deviates from setpoint by more than 2 gpm for 2 seconds and FY5281 = 100% while transfer in progress  Shutdown (blocked valve in loadout)

FI5281 < 0.5 gpm and FY5281 = 100% for 2 seconds  Shutdown (pump protection)

Any pump failure  Hold

Any valve failure  Hold

#### Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Product Storage 3 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-5300 | QA Tank 3 agitator | Mix the liquid product in the QA tank to keep uniform |
| F-5302 | Product filter | Removes impurities from product. |
| P-5301 | QA Pump 3 | Centrifugal pump that transfers liquid product from QA tank into any storage tank. |
| T-5300 | QA Tank 3 | 10,000 gallon storage tank to collect product. When enough product is in the tank and product meets QA specifications, it is transferred to one of the storage tanks. |
| T-5310 | Storage Tank #31 | 10,000 gallon storage tank. Product may be stored here until transferred to the truck/rail loadout. |
| T-5320 | Storage Tank #32 | 10,000 gallon storage tank. Product may be stored here until transferred to the truck/rail loadout. |
| T-5330 | Storage Tank #33 | 10,000 gallon storage tank. Product may be stored here until transferred to the truck/rail loadout. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| DPI5302 | Indicator | Pressure drop across F-5302 filters | Monitors pressure drop to indicate when filters need to be changed | 0-150” |  |
| LI5300 | Indicator | Level of QA Tank 3 | Monitor level | 0-100 (units %) |  |
| LI5310 | Indicator | Level of Storage Tank #31 | Monitor level | 0-100 (units %) |  |
| LI5320 | Indicator | Level of Storage Tank #32 | Monitor level | 0-100 (units %) |  |
| LI5330 | Indicator | Level of Storage Tank #33 | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-5300 | Motor | QA tank 3 agitator | Mixes liquid product in QA tank | Automatic on/off control with deadband. Off when level falls below 10%, On when level rises above 15% |
| P-5301 | Motor | QA Pump 3 | Pumps liquid product from QA tank into any storage tank | This pump should not run if: LI5500<2% or DPI5600>140” |
| XV5300 | Valve | QA Tank 3 Discharge Valve | Controls flow out of QA Tank |  |
| XV5303 | Valve | Loadout Header Rinse Inlet Valve | Admits liquid flushed through header |  |
| XV531l | Valve | Storage Tank #31 Feed Valve | Controls flow into Storage Tank #31 |  |
| XV5321 | Valve | Storage Tank #32 Feed Valve | Controls flow into Storage Tank #32 |  |
| XV5331 | Valve | Storage Tank #33 Feed Valve | Controls flow into Storage Tank #33 |  |
| XV5380 | Valve | Loadout Header Rinse Return Valve | Returns liquid flushed through header to drain |  |

## Unit Operation Interactions

Ion Exchange #5 and #6 Units Liquid product is received from the ion exchange #5 and #6 units into the QA tank 3. This unit has no control over the ion exchange units, except to shut them down when the QA level 3 gets too high.

CIP 2 Unit The product storage unit requests CIP 2 water. When CIP_2 is granted, CIP_2 water is directed to the QA discharge pump, and the storage header valves are properly set to transfer the remaining product in the header to one of the tanks and then return the cleaning water to the CIP_2 tank. When the flush is finished, then the CIP_2 system is requested to return to its normal online/recycle operation.

Storage Loadout 3 Unit When requested by the operator, the product from one of the tanks, is directed to one of the stations in the truck/rail loadout 3.

## Product Storage 3 Operational States

	Transfer - Transfers the entire contents of the QA tank 3 to desired destination tank. Do not allow this operation to start if Transfer is in operation. Steps:

Ask for operator verification that destination selected

Check QA Tank Level > 5%

If destination tank is more than 80% full, abort operation (jump to last step)

Close all valves

Open appropriate tank inlet valve (XV53x1)

Open XV5300

Start P-5301

Wait until destination tank is full (level > 95%), or QA Tank 3 is empty (level < 3%)

Shut down the system

	Flush - Flushes the storage tank header with rinse water. Can only be requested if already shutdown

If QA tank level < 5% (enough to recharge product header), abort (go to last step)

Open XV5303

If CIP_2 System is in shutdown or e-shutdown,

Request CIP_2 System to go online/recycle and wait for CIP_2 system online

Request CIP_2 System to set Feed Storage Path and wait for CIP_2 path set

If Storage Tank #13 has a level < 90%, open feed valve to tank #13 XV5231. Otherwise, open rinse return valve XV5380

Start P-5301

If XV5331 opened, wait 45 seconds for product to be flushed into tank #33. Then open XV5380 and close XV5331

Flush for 10 minutes

Request CIP_2 system to go online/recycle and wait for XV6202 to be closed

Close XV5303

Open XV5300

Charge product storage header with product (90 seconds)

Shutdown

- Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off the pump and all storage header valves:

Stop P-5301

Close XV5300

Close XV5303

Close XV5311

Close XV5321

Close XV5331

Close XV5380

	E-Shutdown - Immediately turns off the pump and all storage header valves:

Stop P-5301

Close XV5300, XV5303, XV5311, XV5321, XV5331, XV5380

### Product Storage 3 Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI5300 > 90 (units in %) for 20 seconds  Alarm

LI5300 > 95% for 20 seconds  Shut down process (not implemented)

LI5300 < 2% for 20 seconds while transfer in progress  Shutdown

DPI5302 > 130” for 1 second  Alarm

DPI5302 > 140” for 1 second  Shutdown

LI5310 > 95% for 60 seconds while in transfer to T-5310  Shutdown

LI5320 > 95% for 60 seconds while in transfer to T-5320  Shutdown

LI5330 > 95% for 60 seconds while in transfer to T-5330   Shutdown

CIP_2 System not in Feed Storage Path when unit in steps where CIP_2 system used  E-Shutdown

Lose heartbeat with CIP_2 System for 10 seconds when unit in steps where CIP_2 system used  E-Shutdown

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Storage 3 Loadout Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| P-5381 | Loadout Pump | Centrifugal pump that transfers liquid product from any storage tank to the truck/rail loadout 3 |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| FIC5381 | Loop | Loadout transfer flow control | Controls feed rate of transfer to truck/rail loadout 3 | 0-200 gpm, Fail closed, direct acting |  |
| FQI5381 | Indicator | Totalized loadout product flow | Measures amount of product transferred to loadout 3 |  |  |
| LI5310 | Indicator | Level of Storage Tank #31 | Monitor level | 0-100 (units %) |  |
| LI5320 | Indicator | Level of Storage Tank #32 | Monitor level | 0-100 (units %) |  |
| LI5330 | Indicator | Level of Storage Tank #33 | Monitor level | 0-100 (units %) |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| P-5381 | Motor | Loadout Pump | Pumps liquid product from any storage tank to the truck/rail loadout | This pump should not run if PV:FIC5381<0.5 gpm and VO:FIC5381=100% |
| XV5312 | Valve | Storage Tank #31 Discharge Valve | Controls flow out of Storage Tank #31 |  |
| XV5322 | Valve | Storage Tank #32 Discharge Valve | Controls flow out of Storage Tank #32 |  |
| XV5332 | Valve | Storage Tank #33 Discharge Valve | Controls flow out of Storage Tank #33 |  |
| XV5391 | Valve | Truck Load Station #1 Valve | Controls flow into truck at station #1 |  |
| XV5392 | Valve | Truck Load Station #2 Valve | Controls flow into truck at station #2 |  |
| XV5396 | Valve | Rail Load Station #1 Valve | Controls flow into railcar at station #1 |  |
| XV5397 | Valve | Rail Load Station #2 Valve | Controls flow into railcar at station #2 |  |

## Unit Operation Interactions

Storage Unit 3 This unit loads out product from the product storage 3 unit. This unit has no control over the product storage unit.

## Storage 3 Loadout Unit Operational States

	Transfer - Transfers the entire contents of source tank to the desired station:

Ask for operator verification that source and destination selected

If source tank is less than 3% full, abort operation

Close all valves

(Start up loadout system)

Reset loadout flow totalizer, FQI5381

Request amount of product from operator

Open appropriate load station valve (XV5391, XV5392, XV5396, or XV5397)

Open appropriate tank outlet valve (XV53x2)

Start P-5381

Initialize the loadout flow controller to operator-adjusted setpoint

Wait until source tank is empty (level <3%) or FQI5381 totalized flow >= desired

Shut down the system

	Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off the pump and all discharge header valves:

Stop P-5381

Set FIC5381 to manual, -10% output

Close XV5312

Close XV5322

Close XV5332

Close XV5391

Close XV5392

Close XV5396

Close XV5397

	E-Shutdown - Immediately turns off the pump and all discharge header valves:

Stop P-5381

Set FIC5381 to manual, -10% output

Close XV5312, XV5322, XV5332, XV5391, XV5392, XV5396, XV5397

### Storage 3 Loadout Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

LI5310 < 3% for 20 seconds and T5310 Transfer in progress  Shut down

LI5320 < 3% for 20 seconds and T5320 Transfer in progress  Shut down

LI5330 < 3% for 20 seconds and T5330 Transfer in progress  Shut down

FI5381 deviates from setpoint by more than 2 gpm for 10 seconds while transfer in progress  Alarm

FI5381 deviates from setpoint by more than 2 gpm for 3 minutes while transfer in progress  Shutdown

FI5381 deviates from setpoint by more than 2 gpm for 2 seconds and FY5381 = 100% while transfer in progress  Shutdown (blocked valve in loadout)

FI5381 < 0.5 gpm and FY5381 = 100% for 2 seconds  Shutdown (pump protection)

Any pump failure  Hold

Any valve failure  Hold

#### Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

# Clean-In-Place (CIP) 1 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-6000 | CIP 1 Tank agitator | Mix the cleaning water in the CIP tank to keep uniform |
| H-6000 | CIP 1 Heat Exchanger | Plate and frame heat exchanger to heat up the CIP water with 50# steam. |
| P-6000 | CIP 1 Pump | Centrifugal pump that recirculates cleaning water through the heat exchanger, or transfers it to the reactor, ion exchange, or product storage unit. |
| T-6000 | CIP 1 Tank | 4,000 gallon storage tank to store cleaning water and to mix in soda ash. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI6000 | Indicator | pH of CIP 1 Tank | Monitor pH to determine proper make-up and when new make-up needs to be formulated | 0-14 |  |
| FIC6050 | Loop | Hot water supply flow control | Controls feed rate of hot water to CIP 1 tank | 0-100 gpm, Fail closed, direct acting |  |
| FQI6050 | Indicator | Totalized hot water flow | Measures amount of hot water placed into CIP 1 tank |  |  |
| LI6000 | Indicator | Level of CIP 1 Tank | Monitor level | 0-100 (units %) |  |
| TIC6000 | Loop | CIP 1 Tank Recirc-ulating water temp-erature control | Controls feed rate of steam supply to heat exchanger | 70-200 deg F, Fail open, reverse acting |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-6000 | Motor | CIP 1 tank agitator | Mixes water and ash in CIP 1 tank to maintain uniform temperature | Automatic on/off control with deadband. Off when level falls below 10%, On when level rises above 15% |
| P-6000 | Motor | CIP 1 Pump | Pumps water from CIP 1 tank | This pump should not run if: LI6000<2% |
| XV6001 | Valve | CIP 1 Tank Recycle Valve | Controls flow out of CIP 1 Tank and through heat exchanger |  |
| XV6002 | Valve | CIP 1 to Storage Valve | Controls flow of CIP 1 water into Storage Unit |  |
| XV6003 | Valve | CIP 1 to Reactor 1 Equipment Valve | Controls flow of CIP 1 water to Reactor 1 Unit |  |
| XV6004 | Valve | CIP 1 to Ion Exchange 1 & 2 Valve | Controls flow of CIP 1 water to Ion Exchange 1 & 2 |  |
| XV6005 | Valve | CIP 1 to Waste Tank | Controls flow of CIP 1 water into Waste tank |  |
| XV6006 | Valve | CIP 1 to Reactor 2 Equipment Valve | Controls flow of CIP 1 water to Reactor 2 Unit |  |

## Unit Operation Interactions

Reactor 1 and 2 Units When requested by the reactor 1 or 2 units, the valve paths are set to direct CIP water to the reactor process equipment and then returned to the CIP tank. When the reactor piping flush is finished, then the CIP system returns to its normal online/recycle operation.

Ion Exchange Unit When requested by the ion exchange unit, the valve paths are set to direct CIP water to the ion exchange #1 or #2 equipment and then returned to the CIP tank. When the ion exchange piping flush is finished, then the CIP system returns to its normal online/recycle operation.

Product Storage 1 Unit When requested by the product storage 1 unit, the valve paths are set to direct CIP water to the product storage 1 unit QA discharge pump and then to be returned to the CIP tank. When the product storage flush is finished, then the CIP system returns to its normal online/recycle operation.

Waste Tank Unit When requested by the operator, the valve paths are set to direct CIP water to the waste tank, thereby emptying the CIP tank. When the tank is empty, the CIP system starts make-up.

Soda Ash Unit Loads soda ash when requested by this unit.

50# Steam Supply Used by heat exchanger to maintain CIP water temperature.

Hot Water Supply Used to get water supply to recharge CIP system cleaning water.

## CIP 1 Unit Operational States

	Online/Recycle - Starts up the system and starts recycling the cleaning water through the heat exchanger to maintain its temperature:

If CIP 1 Tank level < 20%, wait.

Open CIP 1 Recycle Valve, XV6001

Close CIP 1 to Storage Valve, XV6002

Close CIP 1 to Reactor 1 Valve, XV6003

Close CIP 1 to Ion Exchange Valve, XV6004

Close CIP 1 to Waste Valve, XV6005

Close CIP 1 to Reactor 2 Valve, XV6006

Put Recirculating temperature control, TIC6000, in auto, setpoint=150 F

Start CIP 1 Pump, P-6000

	Reactor 1 Path - Sets the path to direct CIP 1 water to the Reactor unit, initiated by Reactor 1 Flush sequence, or operator. If commanded by operator, only allowed when in online/recycle. Not allowed when pH alarm ON.

If CIP 1 Tank level < 20%, wait.

Put TIC6000 in manual, output = 0%

Open CIP 1 to Reactor 1 Valve, XV6003

Close CIP 1 Recycle Valve, XV6001

Close CIP 1 to Storage Valve, XV6002

Close CIP 1 to Ion Exchange Valve, XV6004

Close CIP 1 to Waste Valve, XV6005

Close CIP 1 to Reactor 2 Valve, XV6006

Start CIP 1 Pump, P-6000

	Reactor 2 Path - Sets the path to direct CIP 1 water to the Reactor 2 unit, initiated by Reactor 2 Flush sequence, or operator. If commanded by operator, only allowed when in online/recycle. Not allowed when pH alarm ON.

If CIP 1 Tank level < 20%, wait.

Put TIC6000 in manual, output = 0%

Open CIP 1 to Reactor 2 Valve, XV6006

Close CIP 1 Recycle Valve, XV6001

Close CIP 1 to Storage Valve, XV6002

Open CIP 1 to Reactor 1 Valve, XV6003

Close CIP 1 to Ion Exchange Valve, XV6004

Close CIP 1 to Waste Valve, XV6005

Start CIP 1 Pump, P-6000

	Ion Exchange Path - Sets the path to direct CIP water to the Ion Exchange #1 and #2 area, initiated by either Ion Exchange Flush sequence, or operator. If commanded by operator, only allowed when in online/recycle. Not allowed when pH alarm ON.

If CIP 1 Tank level < 20%, wait.

Put TIC6000 in manual, output = 0%

Open CIP 1 to Ion Exchange Valve, XV6004

Close CIP 1 Recycle Valve, XV6001

Close CIP 1 to Storage Valve, XV6002

Close CIP 1 to Reactor 1 Valve, XV6003

Close CIP 1 to Waste Valve, XV6005

Close CIP 1 to Reactor 2 Valve, XV6006

Start CIP 1 Pump, P-6000

	Product Storage 1 Path - Sets the path to direct CIP water to the Product Storage 1 unit, initiated by Product Storage Flush sequence, or operator. If commanded by operator, only allowed when in online/recycle. Not allowed when pH alarm ON.

If CIP 1 Tank level < 20%, wait.

###### Put TIC6000 in manual, output = 0%

Open CIP 1 to Storage Valve, XV6002

Close CIP 1 Recycle Valve, XV6001

Close CIP 1 to Reactor 1 Valve, XV6003

Close CIP 1 to Ion Exchange Valve, XV6004

Close CIP 1 to Waste Valve, XV6005

Close CIP 1 to Reactor 2 Valve, XV6006

Start CIP 1 Pump, P-6000

	To Waste Tank - Sets the path to direct CIP 1 water to the Waste Tank area, initiated by operator:

If Waste Tank level > 70%, abort (not implemented).

Put TIC6000 in manual, output = 0%

Open CIP 1 to Waste Valve, XV6005

Close CIP 1 Recycle Valve, XV6001

Close CIP 1 to Storage Valve, XV6002

Close CIP 1 to Reactor 1 Valve, XV6003

Close CIP 1 to Ion Exchange Valve, XV6004

Close CIP 1 to Reactor 2 Valve, XV6006

Start CIP 1 Pump, P-6000

Wait until CIP 1 Tank level < 2% for 10 minutes

Initiate CIP Make-up

	CIP Make-up - Makes up a new batch of cleaning water from the hot water supply and soda ash from hopper, initiated by operator. Initiation only allowed if CIP tank is online/recycle, to waste tank, hold, shutdown, or e-shutdown:

If CIP 1 Tank level >= 80%, abort.

Open CIP 1 Recycle Valve, XV6001

###### Close CIP 1 to Storage Valve, XV6002

Close CIP 1 to Reactor 1 Valve, XV6003

Close CIP 1 to Ion Exchange Valve, XV6004

Close CIP 1 to Waste Valve, XV6005

Close CIP 1 to Reactor 2 Valve, XV6006

Initialize FQI6000

Put Hot Water Flow Controller FIC6050 in auto, setpoint = 100 gpm

Wait for CIP 1 Tank level >= 20%

Start CIP 1 Pump, P-6000

Put Heat Exchanger Temperature Controller TIC6000 in auto, setpoint = 150 F

Wait for CIP 1 Tank level >= 90%

Put FIC6050 in manual, output = 0%

Initiate Soda Ash B-6000 Start Transfer and wait for it to start

Wait for CIP 1 Tank pH AI6000 >= 9

Initiate Soda Ash B-6000 Shutdown and wait for it to shut down

Wait 15 minutes for soda ash to disperse in cleaning water

Initiate Online/Recycle

	Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off the pump and closes all valves:

Stop P-6000

Set TIC6000 to manual, 0% output

Set FIC6050 to manual, 0% output

Close XV6002

Close XV6003

Close XV6004

Close XV6005

Close XV6006

Close XV6001

	E-Shutdown - Immediately turns off the pump and closes all valves:

Stop P-6000

Set TIC6000 to manual, 0% output

Set FIC6050 to manual, 0% output

Close XV6001, XV6002, XV6003, XV6004, XV6005, XV6006

### CIP 1 Unit Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

AI6000 < 7.25 for 2 minutes and in Online/Recycle or Product Storage 1 Path or Reactor 1 Path or Reactor 2 Path or Ion Exchange Path  pH Alarm (need to empty CIP tank and do CIP make-up)

LI6000 > 90% for 20 seconds  Alarm

LI6000 < 10% for 10 seconds and in Online/Recycle or Product Storage 1 Path or Reactor 1 Path or Reactor 2 Path or Ion Exchange Path  Alarm

LI6000 < 2% for 10 seconds and in Online/Recycle or Product Storage 1 Path or Reactor 1 Path or Reactor 2 Path or Ion Exchange Path  Shutdown

FI6050 deviates from setpoint by more than 2 gpm for 10 seconds while filling CIP tank with hot water  Alarm

FI6050 deviates from setpoint by more than 2 gpm for 3 minutes while filling CIP tank with hot water  Shutdown

TIC6000 PV deviates from setpoint by more than 10 F for 1 minute while online/recycling or makeup  Alarm

TIC6000 PV deviates from setpoint by more than 10 F for 10 minutes while online/recycling or makeup  Shutdown

TIC6000 PV deviates from setpoint by more than 10 F for 1 minute while online/recycling or makeup and TY6000 = 100%  Shutdown (loss of steam)

Any pump failure  Hold

Any valve failure  Hold

Soda Ash shuts down while in CIP Makeup  Hold

QA Tank 1 not in Flush while in Product Storage Path 1  Online/Recycle

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

Shutdown of unit using CIP_1  Shutdown

Lose heartbeat to Soda Ash for 10 seconds when transferring ash  Hold

Lose heartbeat with unit using CIP_1 when unit using CIP_1 for 10 seconds   Shutdown

Shutdown of CIP_1 should trigger shutdown of any unit using CIP_1 (during _Path state)

# Soda Ash Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| B-6100 | Soda Ash Storage Hopper | 300 pound storage hopper. Soda ash that is added to the cleaning water is transferred from this tank. |
| C-6100 | Soda Ash Screw Conveyor | Conveys soda ash from the storage hopper to the slide gate. |
| G-6000 | CIP Tank Slide Gate | Soda ash enters the CIP tank through this gate. |
| L-6100 | Soda Ash Airlock | Soda ash air lock discharge valve from storage hopper. |

### Analog Instrument and Control Point Listing

Analog Control Points

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| C-6100 | Conveyor | Soda Ash Screw Conveyor | Moves soda ash from hopper to CIP tank slide gate. |  |
| L-6100 | Motor | Soda Ash air lock | Discharges soda ash from hopper |  |
| LSL6100 | Level Switch | Soda Ash level | Indicates low level |  |
| M-6000 | Motor | CIP Tank Slide Gate Motor | Opens/closes CIP tank slide gate |  |
| SS6100 | Speed Switch | C-6100 Speed Switch | Indicates that conveyor is stopped |  |
| ZSC6000 | Limit Switch | ZS6000 slide gate switch | Indicates slide gate is closed |  |
| ZSO6000 | Limit Switch | ZS6000 slide gate switch | Indicates slide gate is open |  |

### Unit Operation Interactions

CIP Tank Unit Requests start transfer and shutdown of this unit.

## Soda Ash Unit States

	Start Transfer - Starts up the transfer of soda ash to the CIP tank:

Open CIP Tank Slide Gate G-6000

Start Soda Ash Screw Conveyor C-6100

Start Soda Ash Airlock L-6100

	Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off the pump and closes all valves:

Stop Soda Ash Airlock L-6100

Wait 30 seconds for C-6100 to clear

Stop Soda Ash Screw Conveyor C-6100

Close CIP Tank Slide Gate G-6000

	E-Shutdown - Immediately turns off all motors and closes the slide gate:

Stop L-6100, C-6100

Close G-6000

### Soda Ash Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

L-6100 failure for 1 second  Shutdown

C-6100 failure for 1 second  E-Shutdown

G-6000 failure for 1 second  E-Shutdown

SS6100 indicates conveyor off  Alarm

LSL6100 indicates low bin level for 2 seconds  Alarm

LSL6100 indicates low bin level for 20 seconds and transfer started  Shutdown

CIP_1 shutdown for 1 second and in transfer state  Shutdown

Lose heartbeat to CIP_1 for 10 seconds and in transfer state  E-Shutdown

Standard Aux, HOA, overload alarms on motors

Standard Fail to Open, Fail to Close alarms on slide gate

# Clean-In-Place (CIP) 2 Unit

## Major Equipment

| TAG | DESCRIPTION | PURPOSE |
| --- | --- | --- |
| A-6200 | CIP 2 Tank agitator | Mix the cleaning water in the CIP tank to keep uniform |
| H-6200 | CIP 2 Heat Exchanger | Plate and frame heat exchanger to heat up the CIP water with 50# steam. |
| P-6200 | CIP 2 Pump | Centrifugal pump that recirculates cleaning water through the heat exchanger, or transfers it to the reactor, ion exchange, or product storage unit. |
| T-6200 | CIP 2 Tank | 4,000 gallon storage tank to store cleaning water and to mix in caustic. |
| T-6300 | CIP 2 Caustic Storage Tank | 500 gallon storage tank to store caustic. |

### Analog Instrument and Control Point Listing

Analog Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | OTHER INFO | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- | --- |
| AI6200 | Indicator | pH of CIP 2 Tank | Monitor pH to determine proper make-up and when new make-up needs to be formulated | 0-14 |  |
| FIC6250 | Loop | Hot water supply flow control | Controls feed rate of hot water to CIP 2 tank | 0-100 gpm, Fail closed, direct acting |  |
| FQI6250 | Indicator | Totalized hot water flow | Measures amount of hot water placed into CIP 2 tank |  |  |
| LI6200 | Indicator | Level of CIP 2 Tank | Monitor level | 0-100 (units %) |  |
| TIC6200 | Loop | CIP 2 Tank Recirc-ulating water temp-erature control | Controls feed rate of steam supply to heat exchanger | 70-200 deg F, Fail open, reverse acting |  |

### Discrete Instrument and Control Point Listing

Discrete Control Points

| TAG | TYPE | DESCRIPTION | PURPOSE | SEQUENCE BASED INTERLOCKS |
| --- | --- | --- | --- | --- |
| A-6200 | Motor | CIP 2 tank agitator | Mixes water and ash in CIP 2 tank to maintain uniform temperature | Automatic on/off control with deadband. Off when level falls below 10%, On when level rises above 15% |
| P-6200 | Motor | CIP 2 Pump | Pumps water from CIP 2 tank | This pump should not run if: LI6200<2% |
| P-6302 | Motor | Caustic Storage Pump | Pumps water from caustic storage | This pump should not run if: LI6300<2% |
| XV6201 | Valve | CIP 2 Tank Recycle Valve | Controls flow out of CIP 2 Tank and through heat exchanger |  |
| XV6202 | Valve | CIP 2 to Storage 3 Valve | Controls flow of CIP 2 water to Storage 3 Unit |  |
| XV6203 | Valve | CIP 2 to Reactor 4 Equipment Valve | Controls flow of CIP 2 water to Reactor 1 Unit |  |
| XV6204 | Valve | CIP 2 to Ion Exchange 5 & 6 Valve | Controls flow of CIP 2 water to Ion Exchange 1 & 2 |  |
| XV6205 | Valve | CIP 2 to Waste Tank | Controls flow of CIP 2 water into Waste tank |  |
| XV6301 | Valve | Caustic Storage Outlet Valve | Controls flow out of caustic storage tank |  |

## Unit Operation Interactions

Reactor 4 Unit When requested by the reactor 4 unit, the valve paths are set to direct CIP water to the reactor process equipment and then returned to the CIP tank. When the reactor piping flush is finished, then the CIP system returns to its normal online/recycle operation.

Ion Exchange Unit When requested by the ion exchange unit, the valve paths are set to direct CIP water to the ion exchange #5 or #6 equipment and then returned to the CIP tank. When the ion exchange piping flush is finished, then the CIP system returns to its normal online/recycle operation.

Waste Tank Unit When requested by the operator, the valve paths are set to direct CIP water to the waste tank, thereby emptying the CIP tank. When the tank is empty, the CIP system starts make-up.

50# Steam Supply Used by heat exchanger to maintain CIP water temperature.

Hot Water Supply Used to get water supply to recharge CIP system cleaning water.

## CIP 2 Unit Operational States

	Online/Recycle - Starts up the system and starts recycling the cleaning water through the heat exchanger to maintain its temperature:

If CIP 2 Tank level < 20%, wait.

Open CIP 2 Recycle Valve, XV6201

Close CIP 2 to Storage 3 Valve, XV6202

Close CIP 2 to Reactor 1 Valve, XV6203

Close CIP 2 to Ion Exchange Valve, XV6204

Close CIP 2 to Waste Valve, XV6205

Put Recirculating temperature control, TIC6200, in auto, setpoint=150 F

Start CIP 2 Pump, P-6200

	Reactor 4 Path - Sets the path to direct CIP 2 water to the Reactor 4 unit, initiated by Reactor 4 Flush sequence, or operator. If commanded by operator, only allowed when in online/recycle. Not allowed when pH alarm ON.

If CIP 2 Tank level < 20%, wait.

Put TIC6200 in manual, output = 0%

Open CIP 2 to Reactor 4 Valve, XV6203

Close CIP 2 Recycle Valve, XV6201

Close CIP 2 to Storage 3 Valve, XV6202

Close CIP 2 to Ion Exchange Valve, XV6204

Close CIP 2 to Waste Valve, XV6205

Start CIP 2 Pump, P-6200

	Ion Exchange Path - Sets the path to direct CIP water to the Ion Exchange #5 and #6 area, initiated by either Ion Exchange Flush sequence, or operator. If commanded by operator, only allowed when in online/recycle. Not allowed when pH alarm ON.

If CIP 2 Tank level < 20%, wait.

Put TIC6200 in manual, output = 0%

Open CIP 2 to Ion Exchange Valve, XV6204

Close CIP 2 Recycle Valve, XV6201

Close CIP 2 to Storage 3 Valve, XV6202

Close CIP 2 to Reactor 4 Valve, XV6203

Close CIP 2 to Waste Valve, XV6205

Start CIP 2 Pump, P-6200

	Storage 3 Path - Sets the path to direct CIP water to the Storage Tank #3 unit, initiated by Storage Tank #3 Flush sequence, or operator. If commanded by operator, only allowed when in online/recycle. Not allowed when pH alarm ON.

If CIP 2 Tank level < 20%, wait.

Put TIC6200 in manual, output = 0%

Open CIP 2 to Storage 3 Valve, XV6202

Close CIP 2 Recycle Valve, XV6201

Close CIP 2 to Reactor 4 Valve, XV6203

Close CIP 2 to Ion Exchange Valve, XV6204

Close CIP 2 to Waste Valve, XV6205

Start CIP 2 Pump, P-6200

	To Waste Tank - Sets the path to direct CIP 2 water to the Waste Tank, initiated by operator:

If Waste Tank level > 70%, abort (not implemented).

Put TIC6200 in manual, output = 0%

Open CIP 2 to Waste Valve, XV6205

Close CIP 2 Recycle Valve, XV6201

Close CIP 2 to Storage 3 Valve, XV6202

Close CIP 2 to Reactor 4 Valve, XV6203

Close CIP 2 to Ion Exchange Valve, XV6204

Start CIP 2 Pump, P-6200

Wait until CIP 2 Tank level < 2% for 10 minutes

Initiate CIP Make-up

	CIP Make-up - Makes up a new batch of cleaning water from the hot water supply and caustic tank, initiated by operator. Initiation only allowed if CIP tank is online/recycle, to waste tank, hold, shutdown, or e-shutdown:

If CIP 2 Tank level >= 80%, abort.

Open CIP 2 Recycle Valve, XV6201

Close CIP 2 to Storage 3 Valve, XV6202

Close CIP 2 to Reactor 4 Valve, XV6203

Close CIP 2 to Ion Exchange Valve, XV6204

Close CIP 2 to Waste Valve, XV6205

Initialize FQI6200

Put Hot Water Flow Controller FIC6250 in auto, setpoint = 100 gpm

Wait for CIP 2 Tank level >= 20%

Start CIP 2 Pump, P-6200

Put Heat Exchanger Temperature Controller TIC6200 in auto, setpoint = 150 F

Wait for CIP 2 Tank level >= 90%

Put FIC6250 in manual, output = 0%

Open XV6301

Start P-6302

Wait for CIP 2 Tank pH AI6200 >= 9

Stop P-6302

Close XV6301

Wait 5 minutes for caustic to disperse in cleaning water

Initiate Online/Recycle

	Hold - Allow the operator access to manipulate discrete points in the system, from local field interfaces, while the process system is running.

	Shutdown - Turns off the pump and closes all valves:

Stop P-6200

Stop P-6302

Set TIC6200 to manual, 0% output

Set FIC6250 to manual, 0% output

Close XV6301

Close XV6203

Close XV6202

Close XV6204

Close XV6205

Close XV6201

	E-Shutdown - Immediately turns off the pump and closes all valves:

Stop P-6200, P6302

Set TIC6200 to manual, 0% output

Set FIC6250 to manual, 0% output

Close XV6301, XV6201, XV6202, XV6203, XV6204, XV6205

### CIP 2 Unit Abnormal Conditions

The following conditions are abnormal and will cause the indicated action.

AI6200 < 7.25 for 2 minutes and in Online/Recycle or Reactor 4 Path or Ion Exchange Path  pH Alarm (need to empty CIP tank and do CIP make-up)

LI6200 > 90% for 20 seconds  Alarm

LI6200 < 10% for 10 seconds and in Online/Recycle or Reactor 4 Path or Ion Exchange Path  Alarm

LI6200 < 2% for 10 seconds and in Online/Recycle or or Reactor 4 Path or Ion Exchange Path  Shutdown

FI6250 deviates from setpoint by more than 2 gpm for 10 seconds while filling CIP tank with hot water  Alarm

FI6250 deviates from setpoint by more than 2 gpm for 3 minutes while filling CIP tank with hot water  Shutdown

TIC6200 PV deviates from setpoint by more than 10 F for 1 minute while online/recycling or makeup  Alarm

TIC6200 PV deviates from setpoint by more than 10 F for 10 minutes while online/recycling or makeup  Shutdown

TIC6200 PV deviates from setpoint by more than 10 F for 1 minute while online/recycling or makeup and TY6200 = 100%  Shutdown (loss of steam)

Any pump failure  Hold

Any valve failure  Hold

Standard Aux, HOA, overload alarms on pumps

Standard Fail to Open, Fail to Close alarms on valves

Shutdown of unit using CIP_2  Shutdown

Lose heartbeat with unit using CIP_2 when unit using CIP_2 for 10 seconds   Shutdown

Shutdown of CIP_2 should trigger shutdown of any unit using CIP_2 (during _Path state)

# Revision History

Rev 0	29 Mar 2005	First release

Rev 1	25 Mar 2007	Fix typos.

Rev 2 	3 Sep 2007	Added Ion Exchange #2

Rev 3 	15 Jan 2008	Fix typos.

Rev 4 	2 Sep 2013	Added Dry Add Makeup unit.

Rev 4.1 	7 Sep 2013	Fix typo - add FIC3210 to Reactor 2.

Rev 5.0	3 Sep 2014	Added Wet Additive Unit, Powder Unload Cell, React 3, Ion Exchange 3 & 4, Product Storage 2

Rev 5.1	11 Sep 2014	Fix typos

Rev 5.2	15 Sep 2014	Fix typos in dry additive and wet additive units

Rev 5.3	22 Sep 2014	Conveyor alignment switch and plug switch states described.

Rev 5.4	29 Sep 2014	Add XV2166 to Wet Ingredient Storage

Rev 5.5	4 Nov 2014	Fixed Dry Storage Loadin unit operation interactions

Rev 6.0	28 Aug 2016	Added Reactor 4, CIP 2, Ion Exchange 5 & 6, Product Storage 3, and Product Loadout 3. Renumbered equipment tags in Product Storage 1 & 2 and Product Loadout 1 & 2.

Rev 6.1	12 Sep 2016	Fix typos

Rev 6.2	23 Sep 2016	To CIP 2 unit, added missing caustic tank to major equipment and added caustic outlet valve and pump to discrete control points.

Rev 6.3	7 Oct 2016	To Ion_Exc_5 and Ion_Exc_6, added steps in Flush. React_4 typos in analog control points fixed.

Rev 6.4	27 Jan 2017	React_4 needs to use CIP_2 in Flush

Rev 6.5	29 Sep 2017	Clarify unit interactions with Reactors 1 and 2

Rev 6.6	17 Oct 2017	React_2 add prompt for dry ingredient source. Fix React_1 interaction to start Ion_Exc_1 and React_2 interaction to start Ion_Exc_2

Rev 6.7	4 Sep 2018	Correct typos in Blend, React_1, and React_2

Rev 6.8	13 Nov 2018	Minor revs to most units.

Rev 6.9	19 Sep 2019	Correct descriptions in Product Storage 3 and Product Loadout 3

Rev 6.10	17 Oct 2019	Minor revs to many units

Rev 6.11	23 Oct 2020	Minor revs to many units. Added storage unit valves to discrete control points in R/TWet unload, R/TPowder unload, Dry/Wed Additive, Blend, React_3, React_4

Rev 6.12	11 Mar 2021	Revs to React_1 and React_2 abnormal conditions

Rev 7.0	25 Aug 2021	Add abnormal conditions when communication heartbeats are lost

Rev 7.1	22 Dec 2021	Corrections to abnormal conditions involving heartbeats. Corrections to TDry_Unl abnormal conditions.

Rev 7.2	16 Nov 2022	Added XV26x6 valves to Reactor 3 devices. Fix typos in Dry Storage LoadIn and LoadOut.

Rev 7.3	22 Oct 2023	Correction to Flush for Ion_Exc_5 and Ion_Exc_6.