## Sample
0 | T1000_Sample.Step_Num | NOTE: ALL Spare Step Rows are HIDDEN
Operator Initiated .or. Auto Bit
| T1000_Sample.PC_Start .or. T1000_Sample.LTP_Start | Commands | _Msg number
.or. T1000_Sample.Auto_Start
1 | Start Transfer pump P-1001 | P1001.Seq_Start
| Msg: "Waiting for P-1001 to start" |  | 41
P-1001 running
P1001_Aux
2
| Msg: "" |  | 42
3 | Check Unload pump, P-1002
| Msg: "" |  | 43
| P-1002 running |  |  | P-1002 stopped
| P1002_Aux |  |  | /P1002_Aux
4 | Stop Unload pump, P-1002 | P1002.Seq_Stop
| Msg: "Waiting for P-1002 to stop" |  | 44
P-1002 stopped
/P1002_Aux
5
| Msg: "" |  | 45
6 | Close outlet valve NV1001 | NV1001.Seq_Close
| Msg: "Waiting for NV1001 to close" |  | 46
NV1001 closed
NV1001_CloseLS
7
| Msg: "" |  | 47
8 | Open inlet valve NV1002 | NV1002.Seq_Open
| Msg: "Waiting for NV1002 to open" |  | 48
NV1002 open
NV1002_OpenLS
9
| Msg: "" |  | 49
10 | Set Material A flow controller FIC1001 to manual, 0% out | FIC1001.SWM
FIC1001.SO=0
| Msg: "Waiting for FIC1001 in manual, 0% out" |  | 50
FIC1001 out = 0%
FIC1001.OUT = 0
11
| Msg: "" |  | 51
12 | Initiate T1000_Online | T1000_Online.Auto_Start
| Msg: "Waiting for T1000 Online initiated" |  | 12
Online .or. Hold .or. Shutdown .or. E-Shutdown

## Blank
0 | .Step_Num | NOTE: ALL Spare Step Rows are HIDDEN
Operator initiated .or. Auto Bit
|  | Commands | .Msg number
1
| Msg: "" |  | 1
2
| Msg: "" |  | 2
3
| Msg: "" |  | 3
4
| Msg: "" |  | 4
5
| Msg: "" |  | 5
6
| Msg: "" |  | 6
7
| Msg: "" |  | 7
8
| Msg: "" |  | 8
9
| Msg: "" |  | 9
10
| Msg: "" |  | 10
11
| Msg: "" |  | 11
Transfer .or. Hold .or. E-Shutdown .or. Flush

## Sequence Interlocks
Request
Description | Condition | Bit | Action
Hold
P-1001 fails for 1 second | P1001_Any_Fail for | T1000_Hold.Auto_Start | Hold
P1001_FailHold_Tmr (1 sec)
P-1002 fails for 1 second | P1002_Any_Fail for | T1000_Hold.Auto_Start | Hold
P1002_FailHold_Tmr (1 sec)
XV1001 fails for 1 second | NV1001_Any_Fail for | T1000_Hold.Auto_Start | Hold
NV1001_FailHold_Tmr (1 sec)
XV1002 fails for 1 second | NV1002_Any_Fail for | T1000_Hold.Auto_Start | Hold
NV1002_FailHold_Tmr (1 sec)